## Export
Serial Number | Discom | Cluster | Zone | Circle | Division | Sub Division | Sub Station | Feeder Code | Feeder Name | Feeder Category | DTR Name | DTRating | DTR Meter No. | MF | CT Ratio | Average Voltage(Vbn) | Average Voltage(Vrn) | Average Voltage(Vyn) | Max Average CurrentIB * MF | Max Average CurrentIR * MF | Max Average CurrentIY * MF | Neutral Current | Avg Current | KVA_IB | KVA_IR | KVA_IY | Total_KVA | Unbalancing Percent | Unbalancing Status | Overloading Percent | Overloading Status
1 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | K Z plasticfactory 2nd dt18 | 63 | AL1505002 | 20 | 100/5 | 193.3772 | 193.0981 | 0 | 50 | 0 | 95.2 | 4.124 | 48.4 | 9.6689 | 0 | 0 | 9.6689 | 96.69 | Critical | 15.35 | Normal
2 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | Jitendra indian petrol pump DT18 | 25 | AL1505005 | 10 | 50/5 | 238.4738 | 236.1267 | 237.1021 | 19.6 | 0 | 19.4 | 1.9501 | 13 | 4.6741 | 0 | 4.5998 | 9.2739 | 50.77 | Critical | 37.1 | Normal
3 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756COL | COLD_26154422756CLD | Agriculture | Singarpur 1th dt09 | 63 | AL1505007 | 20 | 100/5 | 243.1292 | 0 | 245.7415 | 0 | 0 | 45.8 | 2.29 | 15.2667 | 0 | 0 | 11.255 | 11.255 | 200 | Critical | 17.87 | Normal
4 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIA | KIRAWALI-3_26154424596KW3 | Agriculture | Indian petrol pump dt36 | 63 | AL1505008 | 20 | 100/5 | 201.5816 | 205.8325 | 201.9548 | 0 | 0 | 63.4 | 3.17 | 21.1333 | 0 | 0 | 12.8039 | 12.8039 | 200 | Critical | 20.32 | Normal
5 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | Naresh Enterprises dt08 | 25 | AL1505013 | 10 | 50/5 | 238.9742 | 237.7981 | 237.306 | 33.8 | 0 | 33 | 3.3407 | 22.2667 | 8.0773 | 0 | 7.8311 | 15.9084 | 51.8 | Critical | 63.63 | Normal
6 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | Nangla tithi dt04 | 25 | AL1505014 | 0.100000001 | 50/5 | 182.4045 | 215.1703 | 198.434 | 3.45 | 2.1 | 0.94 | 2.1758 | 2.1633 | 0.6293 | 0.45186 | 0.18653 | 1.2677 | 59.48 | Critical | 5.07 | Normal
7 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | Dhanya cnc work dt29 | 25 | AL1505015 | 10 | 50/5 | 237.6094 | 234.7278 | 241.3208 | 16.3 | 23.4 | 12.8 | 0.93547 | 17.5 | 3.873 | 5.4926 | 3.0889 | 12.4546 | 33.71 | Critical | 49.82 | Normal
8 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Lake view hotel | 25 | AL1505061 | 10 | 50/5 | 190.065 | 191.0019 | 188.4212 | 0 | 33.4 | 36.2 | 3.4884 | 23.2 | 0 | 6.3795 | 6.8208 | 13.2003 | 56.03 | Critical | 52.8 | Normal
9 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | Bus baal fecotry DT09 | 25 | AL1505062 | 10 | 50/5 | 238.107 | 238.0502 | 237.8149 | 19.2 | 36.7 | 19.2 | 1.75 | 25.0333 | 4.5717 | 8.7364 | 4.566 | 17.8741 | 46.6 | Critical | 71.5 | Normal
10 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | G L public school mahur DT17 | 25 | AL1505063 | 10 | 50/5 | 36.0829 | 229.1237 | 200.4589 | 39.6 | 26.8 | 31.5 | 1.1215 | 32.6333 | 1.4289 | 6.1405 | 6.3145 | 13.8839 | 21.35 | Critical | 55.54 | Normal
11 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | Satyvir pipe fecotry DT24 | 25 | AL1505065 | 10 | 50/5 | 0 | 0 | 245.1426 | 0 | 39.1 | 48.2 | 4.4356 | 29.1 | 0 | 0 | 11.8159 | 11.8159 | 65.64 | Critical | 47.26 | Normal
12 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | V k Enterprisesdt03 | 25 | AL1505066 | 20 | 100/5 | 241.4816 | 239.7296 | 239.2047 | 40.2 | 43.6 | 0 | 2.1002 | 27.9333 | 9.7076 | 10.4522 | 0 | 20.1598 | 56.09 | Critical | 80.64 | Warning
13 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Daal mil singapur | 63 | AL1505082 | 20 | 100/5 | 186.2066 | 184.437 | 183.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
14 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Kutumbakam hotal korai | 63 | AL1505084 | 20 | 100/5 | 181.4228 | 178.895 | 179.5879 | 27.6 | 35.4 | 59.4 | 1.4353 | 40.8 | 5.0073 | 6.3329 | 10.6675 | 22.0077 | 45.59 | Critical | 34.93 | Normal
15 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Ninvaya nagriya 4th | 25 | AL1505086 | 10 | 50/5 | 159.4764 | 0 | 162.9792 | 0 | 0 | 78.9 | 7.89 | 26.3 | 0 | 0 | 12.8591 | 12.8591 | 200 | Critical | 51.44 | Normal
16 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Murga form ke pass rasulpur | 63 | AL1505089 | 20 | 100/5 | 191.8168 | 192.3783 | 191.6839 | 7.8 | 10.6 | 3.4 | 0.31432 | 7.2667 | 1.4962 | 2.0392 | 0.65173 | 4.1871 | 45.87 | Critical | 6.65 | Normal
17 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596COL | COLD_26154424596COL | Agriculture | Massy trector assency DT13 | 25 | AL1505142 | 10 | 50/5 | 233.7959 | 0 | 236.5767 | 5.1 | 32.3 | 1.9 | 2.8933 | 13.1 | 1.1924 | 0 | 0.4495 | 1.6419 | 146.56 | Critical | 6.57 | Normal
18 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | GULMOHAR RESORT | 100 | AL1505171 | 40 | 200/5 | 217.8941 | 215.928 | 217.2063 | 164 | 102 | 95.6 | 1.6359 | 120.5333 | 35.7346 | 22.0247 | 20.7649 | 78.5242 | 36.06 | Critical | 78.52 | Normal
19 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Kasturba Gandhi awasiy vidyalay korai | 25 | AL1505176 | 10 | 50/5 | 0 | 181.4462 | 179.5869 | 0 | 9.4 | 25.9 | 2.2709 | 11.7667 | 0 | 1.7056 | 4.6513 | 6.3569 | 120.11 | Critical | 25.43 | Normal
20 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756COL | COLD_26154422756CLD | Agriculture | HP petrol pump nh11 dt08 | 25 | AL1505179 | 10 | 50/5 | 243.5047 | 241.2187 | 243.6115 | 38.7 | 0 | 0 | 3.87 | 12.9 | 9.4236 | 0 | 0 | 9.4236 | 200 | Critical | 37.69 | Normal
21 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | St Peter's school nangla khushiyali | 25 | AL1505182 | 10 | 50/5 | 193.5866 | 190.995 | 195.7108 | 32.6 | 35.7 | 0 | 3.4255 | 22.7667 | 6.3109 | 6.8185 | 0 | 13.1294 | 56.81 | Critical | 52.52 | Normal
22 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756COL | COLD_26154422756CLD | Agriculture | Dr tandan nursing college dt 12 | 25 | AL1505184 | 10 | 50/5 | 237.5892 | 241.4553 | 237.8065 | 14.3 | 44.6 | 49.8 | 3.3207 | 36.2333 | 3.3975 | 10.7689 | 11.8428 | 26.0092 | 37.44 | Critical | 104.04 | Critical
23 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | Jal Nigam gopau | 25 | AL1505186 | 10 | 50/5 | 0 | 91.5111 | 94.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
24 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | Gopau 4th dt15 Baba ki madi ke pass | 100 | AL1506452 | 40 | 200/5 | 191.8331 | 193.8487 | 0.82528 | 69.6 | 54.8 | 104 | 1.093 | 76.1333 | 13.3516 | 10.6229 | 0.085829 | 24.0603 | 36.6 | Critical | 24.06 | Normal
25 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | GULISTAN PARKING | 100 | AL1506458 | 40 | 200/5 | 214.9443 | 214.7533 | 220.9409 | 222.4 | 157.2 | 0.8 | 4.9314 | 126.8 | 47.8036 | 33.7592 | 0.17675 | 81.7396 | 75.39 | Critical | 81.74 | Warning
26 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245PFS | PAHAD FATEHPUR SIKARI_26154432245PFS | Agriculture | NEAR HOSPITAL | 100 | AL1506459 | 40 | 200/5 | 222.0065 | 215.9137 | 221.5545 | 134.8 | 167.2 | 105.6 | 1.3343 | 135.8667 | 29.9265 | 36.1008 | 23.3962 | 89.4234 | 23.06 | Critical | 89.42 | Warning
27 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Jain pura raod 2nd 10 | 25 | AL1506461 | 10 | 50/5 | 176.9656 | 0 | 175.6044 | 40.8 | 0 | 0 | 4.08 | 13.6 | 7.2202 | 0 | 0 | 7.2202 | 200 | Critical | 28.88 | Normal
28 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Nirmala nagriya first | 25 | AL1506462 | 10 | 50/5 | 192.006 | 185.3032 | 0 | 0 | 0 | 54 | 5.4 | 18 | 0 | 0 | 0 | 0 | 200 | Critical | 0 | Normal
29 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Nadanpura Road | 25 | AL1506465 | 10 | 50/5 | 188.8469 | 2.7109 | 206.1552 | 0 | 0 | 3.3 | 0.33 | 1.1 | 0 | 0 | 0.68031 | 0.68031 | 200 | Critical | 2.72 | Normal
30 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Nagar feedar ke pass DT 16 | 25 | AL1506466 | 10 | 50/5 | 205.3686 | 201.638 | 207.9991 | 0 | 0 | 10.4 | 1.04 | 3.4667 | 0 | 0 | 2.1632 | 2.1632 | 200 | Critical | 8.65 | Normal
31 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Ngla bhairavathi 5th | 25 | AL1506469 | 10 | 50/5 | 0 | 183.3208 | 180.2698 | 63.2 | 0 | 0.1 | 6.315 | 21.1 | 0 | 0 | 0.018027 | 0.018027 | 199.53 | Critical | 0.07 | Normal
32 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | AGRAWAL IRON STORE | 100 | AL1506472 | 40 | 200/5 | 0.77787 | 1.8278 | 212.1173 | 0 | 0 | 35.2 | 0.88 | 11.7333 | 0 | 0 | 7.4665 | 7.4665 | 200 | Critical | 7.47 | Normal
33 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | Lal darvaja 1 | 100 | AL1506473 | 40 | 200/5 | 215.4269 | 211.4018 | 209.873 | 271.6 | 135.6 | 321.6 | 4.168 | 242.9333 | 58.5099 | 28.6661 | 67.4952 | 154.6712 | 32.38 | Critical | 154.67 | Critical
34 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | PNB BANK | 100 | AL1506476 | 40 | 200/5 | 186.5751 | 190.7652 | 0 | 28 | 56.4 | 107.6 | 1.7468 | 64 | 5.2241 | 10.7592 | 0 | 15.9833 | 68.12 | Critical | 15.98 | Normal
35 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | WINE SHOP | 100 | AL1506478 | 40 | 200/5 | 187.7796 | 183.1064 | 0.26571 | 42 | 85.6 | 29.2 | 1.2804 | 52.2667 | 7.8867 | 15.6739 | 0.0077586 | 23.5684 | 63.78 | Critical | 23.57 | Normal
36 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | SARASWATI STUDY CENTER | 100 | AL1506489 | 40 | 200/5 | 161.7633 | 1.7427 | 168.6229 | 0 | 178 | 0 | 4.45 | 59.3333 | 0 | 0.3102 | 0 | 0.3102 | 200 | Critical | 0.31 | Normal
37 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Indian oil petrol pump rasulpur | 25 | AL1506491 | 10 | 50/5 | 191.8743 | 191.6022 | 0 | 8 | 18.8 | 41.9 | 2.9995 | 22.9 | 1.535 | 3.6021 | 0 | 5.1371 | 82.97 | Critical | 20.55 | Normal
38 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | PNB BANK | 25 | AL1506492 | 10 | 50/5 | 218.6969 | 207.9643 | 219.9905 | 15.4 | 11.1 | 25 | 1.2326 | 17.1667 | 3.3679 | 2.3084 | 5.4998 | 11.1761 | 45.63 | Critical | 44.7 | Normal
39 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Sugam petrol pump rasulpur | 25 | AL1506494 | 10 | 50/5 | 53.476 | 115.7659 | 187.969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
40 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Nangla gadi | 63 | AL1506495 | 20 | 100/5 | 172.6072 | 171.8479 | 180.0027 | 116.2 | 92.2 | 50.6 | 2.8744 | 86.3333 | 20.057 | 15.8444 | 9.1081 | 45.0095 | 34.59 | Critical | 71.44 | Normal
41 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Khira khas | 25 | AL1506497 | 20 | 100/5 | 153.8397 | 0 | 159.0951 | 51 | 0 | 0 | 2.55 | 17 | 7.8458 | 0 | 0 | 7.8458 | 200 | Critical | 31.38 | Normal
42 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Shri Ram school karahi | 25 | AL1506498 | 10 | 50/5 | 186.76 | 185.4789 | 1.0557 | 0.1 | 34.3 | 0 | 3.425 | 11.4667 | 0.018676 | 6.3619 | 0 | 6.3806 | 199.13 | Critical | 25.52 | Normal
43 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Bakanda khas 1st | 25 | AL1506499 | 10 | 50/5 | 180.3449 | 176.6663 | 180.7582 | 54.1 | 0 | 30.2 | 4.6958 | 28.1 | 9.7567 | 0 | 5.4589 | 15.2156 | 92.53 | Critical | 60.86 | Normal
44 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Churari Road mandit | 25 | AL1506500 | 10 | 50/5 | 181.9927 | 183.153 | 178.9377 | 21.7 | 22.6 | 46.8 | 2.4662 | 30.3667 | 3.9492 | 4.1393 | 8.3743 | 16.4628 | 54.12 | Critical | 65.85 | Normal
45 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632PAT | PATSAL | Agriculture | Patsal jagdish ke khet pr DT08 | 100 | AL1506611 | 40 | 200/5 | 186.741 | 186.0062 | 191.7856 | 0 | 0 | 146 | 3.65 | 48.6667 | 0 | 0 | 28.0007 | 28.0007 | 200 | Critical | 28 | Normal
46 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632PAT | PATSAL | Agriculture | Patsal 1st DT01 | 25 | AL1506614 | 10 | 50/5 | 184.4521 | 1.3929 | 182.9032 | 51.6 | 0 | 0 | 5.16 | 17.2 | 9.5177 | 0 | 0 | 9.5177 | 200 | Critical | 38.07 | Normal
47 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632PAT | PATSAL | Agriculture | Pani ki Tanki dt15 | 25 | AL1506615 | 10 | 50/5 | 189.8381 | 190.6224 | 0 | 0 | 39.8 | 0 | 3.98 | 13.2667 | 0 | 7.5868 | 0 | 7.5868 | 200 | Critical | 30.35 | Normal
48 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Ngla bairavathi 6th | 100 | AL1506616 | 40 | 200/5 | 187.116 | 182.0832 | 184.8291 | 119.2 | 155.2 | 107.2 | 1.0817 | 127.2 | 22.3042 | 28.2593 | 19.8137 | 70.3772 | 22.01 | Critical | 70.38 | Normal
49 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632PAT | PATSAL | Agriculture | Badroli adde pr DT20 | 25 | AL1506619 | 10 | 50/5 | 193.2828 | 187.0065 | 187.6186 | 11 | 35.4 | 49.1 | 3.3426 | 31.8333 | 2.1261 | 6.62 | 9.2121 | 17.9582 | 54.24 | Critical | 71.83 | Normal
50 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632CUM | CHAUMA_26154434632CUM | Agriculture | Giloy 2nd DT 10 | 25 | AL1506621 | 10 | 50/5 | 185.0809 | 186.5387 | 185.7784 | 39.3 | 0 | 25.8 | 3.4586 | 21.7 | 7.2737 | 0 | 4.7931 | 12.0668 | 81.11 | Critical | 48.27 | Normal
51 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632PAT | PATSAL | Agriculture | Bacchon ke ghar per dt12 | 100 | AL1506623 | 40 | 200/5 | 183.878 | 187.6804 | 184.7542 | 189.6 | 82.4 | 146.4 | 2.3355 | 139.4667 | 34.8633 | 15.4649 | 27.048 | 77.3761 | 35.95 | Critical | 77.38 | Normal
52 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632CUM | CHAUMA_26154434632CUM | Agriculture | Pali kirawali 4th dt06 | 25 | AL1506625 | 10 | 50/5 | 187.465 | 190.2422 | 188.5083 | 10.7 | 0 | 0 | 1.07 | 3.5667 | 2.0059 | 0 | 0 | 2.0059 | 200 | Critical | 8.02 | Normal
53 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632PAT | PATSAL | Agriculture | Sonothi primary school DT16 | 100 | AL1506626 | 40 | 200/5 | 186.7724 | 185.2057 | 187.9595 | 92.4 | 134.4 | 74 | 1.3406 | 100.2667 | 17.2578 | 24.8917 | 13.909 | 56.0584 | 34.04 | Critical | 56.06 | Normal
54 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Tehra gate | 100 | AL1506629 | 40 | 200/5 | 187.2746 | 189.764 | 187.4909 | 123.6 | 138.8 | 190 | 1.5064 | 150.8 | 23.1471 | 26.3392 | 35.6233 | 85.1097 | 25.99 | Critical | 85.11 | Warning
55 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632CUM | CHAUMA_26154434632CUM | Agriculture | Pali kirawali 1st dt03 | 25 | AL1506630 | 10 | 50/5 | 102.6359 | 105.6662 | 104.7736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
56 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Jal Nigam first jotana | 63 | AL1506631 | 20 | 100/5 | 184.5797 | 189.373 | 189.904 | 78.4 | 41.8 | 82.6 | 1.9435 | 67.6 | 14.471 | 7.9158 | 15.6861 | 38.0729 | 22.19 | Critical | 60.43 | Normal
57 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Reliance jio tower tf tehra Rawat | 25 | AL1506632 | 10 | 50/5 | 190.1125 | 186.5535 | 194.4083 | 21.3 | 23 | 0.2 | 2.1999 | 14.8333 | 4.0494 | 4.2907 | 0.038882 | 8.379 | 55.06 | Critical | 33.52 | Normal
58 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Mandi Mirza kha rodTower | 25 | AL1506633 | 10 | 50/5 | 0 | 182.5968 | 0 | 44.4 | 71.7 | 17.3 | 4.7112 | 44.4667 | 0 | 13.0922 | 0 | 13.0922 | 61.24 | Critical | 52.37 | Normal
59 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Cua bag2 | 25 | AL1506634 | 10 | 50/5 | 177.6063 | 172.0036 | 192.4326 | 0 | 32.9 | 0 | 3.29 | 10.9667 | 0 | 5.6589 | 0 | 5.6589 | 200 | Critical | 22.64 | Normal
60 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Tera Rawat tubal | 25 | AL1506636 | 10 | 50/5 | 188.9 | 0 | 190.8729 | 39.6 | 0 | 0 | 3.96 | 13.2 | 7.4804 | 0 | 0 | 7.4804 | 200 | Critical | 29.92 | Normal
61 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Jaatfarm house dt28 | 63 | AL1506637 | 20 | 100/5 | 186.243 | 179.2557 | 187.1329 | 52.6 | 86.4 | 0 | 3.7706 | 46.3333 | 9.7964 | 15.4877 | 0 | 25.2841 | 86.47 | Critical | 40.13 | Normal
62 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Near kushvah form house ptw | 25 | AL1506638 | 10 | 50/5 | 185.1475 | 187.6829 | 0 | 18.5 | 15.3 | 0 | 1.7126 | 11.2667 | 3.4252 | 2.8715 | 0 | 6.2968 | 64.2 | Critical | 25.19 | Normal
63 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632CUM | CHAUMA_26154434632CUM | Agriculture | Green field petrol pump DT23 | 25 | AL1506639 | 10 | 50/5 | 182.5302 | 189.3283 | 183.2307 | 65.1 | 1.5 | 60.1 | 6.1253 | 42.2333 | 11.8827 | 0.28399 | 11.0122 | 23.1789 | 54.14 | Critical | 92.72 | Critical
64 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Akosh nagriya 1 | 100 | AL1506643 | 40 | 200/5 | 163.4948 | 161.0334 | 0 | 42 | 90 | 93.6 | 1.2474 | 75.2 | 6.8668 | 14.493 | 0 | 21.3598 | 24.47 | Critical | 21.36 | Normal
65 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Nagla bherawati 2nd | 100 | AL1506644 | 40 | 200/5 | 187.1496 | 1.914 | 174.7574 | 64 | 97.2 | 152 | 1.9243 | 104.4 | 11.9776 | 0.18604 | 26.5631 | 38.7267 | 45.59 | Critical | 38.73 | Normal
66 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Eat plant korai | 25 | AL1506647 | 10 | 50/5 | 179.1057 | 179.8336 | 182.1592 | 28.9 | 36.4 | 0 | 3.329 | 21.7667 | 5.1762 | 6.5459 | 0 | 11.7221 | 67.23 | Critical | 46.89 | Normal
67 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Korai 2nd | 63 | AL1506648 | 20 | 100/5 | 0 | 153.1953 | 155.1619 | 0 | 53.8 | 65.2 | 3.0157 | 39.6667 | 0 | 8.2419 | 10.1166 | 18.3585 | 64.37 | Critical | 29.14 | Normal
68 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Dadugura Rajkumar ghar ke pass | 25 | AL1506649 | 10 | 50/5 | 0 | 185.5473 | 0 | 47.6 | 12.1 | 0 | 4.2851 | 19.9 | 0 | 2.2451 | 0 | 2.2451 | 139.2 | Critical | 8.98 | Normal
69 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632PAT | PATSAL | Agriculture | Patsal Samsan ghat 2nd DT04 | 25 | AL1506650 | 10 | 50/5 | 191.9254 | 0 | 181.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
70 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632CUM | CHAUMA_26154434632CUM | Agriculture | Jiotowar dt13 | 25 | AL1506801 | 10 | 50/5 | 187.1841 | 0 | 184.5507 | 38.2 | 43.5 | 19.8 | 2.1545 | 33.8333 | 7.1504 | 0 | 3.6541 | 10.8045 | 28.57 | Critical | 43.22 | Normal
71 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Shivnagar Mandi Mirza Khan | 63 | AL1506805 | 20 | 100/5 | 184.0563 | 184.1349 | 183.859 | 28.2 | 61.8 | 28 | 1.685 | 39.3333 | 5.1904 | 11.3795 | 5.1481 | 21.718 | 57.12 | Critical | 34.47 | Normal
72 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632CUM | CHAUMA_26154434632CUM | Agriculture | Reliance petrol pump DT 29 | 25 | AL1506808 | 10 | 50/5 | 181.787 | 178.8812 | 183.1235 | 42.4 | 87.3 | 29.6 | 5.2484 | 53.1 | 7.7078 | 15.6163 | 5.4205 | 28.7446 | 64.41 | Critical | 114.98 | Critical
73 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | HP petrol pump Mandi Mirza Khan | 25 | AL1506809 | 10 | 50/5 | 179.9591 | 173.0176 | 212.1589 | 1.1 | 10.2 | 0 | 0.96969 | 3.7667 | 0.19796 | 1.7648 | 0 | 1.9627 | 170.8 | Critical | 7.85 | Normal
74 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Sadhna gas Godam dt29 | 25 | AL1506810 | 10 | 50/5 | 189.343 | 179.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
75 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Pandit meva ram clg DT34 | 25 | AL1506814 | 10 | 50/5 | 187.5363 | 184.3995 | 185.4335 | 0 | 42.9 | 0 | 4.29 | 14.3 | 0 | 7.9107 | 0 | 7.9107 | 200 | Critical | 31.64 | Normal
76 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756SAB | SABJI MANDI_26154422756SMD | Agriculture | Indian oil dt 01 | 100 | AL1506966 | 40 | 200/5 | 229.3798 | 221.6174 | 225.9866 | 5.6 | 55.2 | 61.2 | 1.3214 | 40.6667 | 1.2845 | 12.2333 | 13.8304 | 27.3482 | 50.49 | Critical | 27.35 | Normal
77 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756SAB | SABJI MANDI_26154422756SMD | Agriculture | Kriaoli ramveer ground DT01 | 100 | AL1506969 | 40 | 200/5 | 231.0231 | 227.0367 | 0 | 10 | 15.6 | 10 | 0.14 | 11.8667 | 2.3102 | 3.5418 | 0 | 5.852 | 31.46 | Critical | 5.85 | Normal
78 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463DOOR | DOORA_26154434463DOR | Agriculture | Dura pthhr meal | 25 | AL1506970 | 20 | 100/5 | 184.1437 | 0 | 189.3721 | 59.8 | 0 | 0 | 2.99 | 19.9333 | 11.0118 | 0 | 0 | 11.0118 | 200 | Critical | 44.05 | Normal
79 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | GS feeling stetetion DT24 | 25 | AL1507051 | 10 | 50/5 | 190.4846 | 187.9218 | 191.3056 | 0 | 56.3 | 0 | 5.63 | 18.7667 | 0 | 10.58 | 0 | 10.58 | 200 | Critical | 42.32 | Normal
80 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | SB petrol PUMP DT23 | 25 | AL1507052 | 10 | 50/5 | 190.2147 | 189.6418 | 187.3152 | 0 | 31.6 | 16.3 | 2.7371 | 15.9667 | 0 | 5.9927 | 3.0532 | 9.0459 | 97.91 | Critical | 36.18 | Normal
81 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Jal Nigam jakhadt14 | 25 | AL1507053 | 10 | 50/5 | 169.7629 | 0 | 0 | 22.9 | 0 | 0 | 2.29 | 7.6333 | 3.8876 | 0 | 0 | 3.8876 | 200 | Critical | 15.55 | Normal
82 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Vipin kumar ke ghar ke paas DT39 | 10 | AL1507054 | 10 | 50/5 | 188.5109 | 189.7625 | 191.389 | 17 | 0 | 0 | 1.7 | 5.6667 | 3.2047 | 0 | 0 | 3.2047 | 200 | Critical | 32.05 | Normal
83 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Tata Motors DT22 | 25 | AL1507055 | 10 | 50/5 | 189.3972 | 188.943 | 189.7475 | 14.4 | 10.5 | 10.7 | 0.38039 | 11.8667 | 2.7273 | 1.9839 | 2.0303 | 6.7415 | 21.35 | Critical | 26.97 | Normal
84 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Sks company temporary DT25 | 25 | AL1507056 | 10 | 50/5 | 197.4988 | 188.0402 | 184.9667 | 10.9 | 0 | 50.2 | 4.5735 | 20.3667 | 2.1527 | 0 | 9.2853 | 11.4381 | 146.48 | Critical | 45.75 | Normal
85 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Sakatpur 1th dt02 | 25 | AL1507057 | 10 | 50/5 | 191.3099 | 192.9643 | 190.9043 | 0 | 0 | 20 | 2 | 6.6667 | 0 | 0 | 3.8181 | 3.8181 | 200 | Critical | 15.27 | Normal
86 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Jal Nigam dt13 | 25 | AL1507058 | 10 | 50/5 | 189.1469 | 192.6733 | 191.1176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
87 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Hemalta tibari petrol pump DT29 | 25 | AL1507060 | 10 | 50/5 | 185.6986 | 187.9841 | 190.1797 | 41.1 | 14.5 | 2 | 3.4588 | 19.2 | 7.6322 | 2.7258 | 0.38036 | 10.7383 | 114.06 | Critical | 42.95 | Normal
88 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | Old bijli ghar | 100 | AL1507062 | 40 | 200/5 | 223.6494 | 227.122 | 224.6642 | 83.6 | 25.2 | 0.4 | 1.8496 | 36.4 | 18.6971 | 5.7235 | 0.089866 | 24.5104 | 129.67 | Critical | 24.51 | Normal
89 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DRE | DREAM CITY_26154424669DRM | Agriculture | DREAM CITY-7 | 250 | AL1507064 | 80 | 400/5 | 245.1824 | 246.0318 | 245.0855 | 45.6 | 92 | 69.6 | 0.50239 | 69.0667 | 11.1803 | 22.6349 | 17.058 | 50.8732 | 33.2 | Critical | 20.35 | Normal
90 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756SAB | SABJI MANDI_26154422756SMD | Agriculture | HINDUSTAN TRADERS FRONT OF TEHSIL | 100 | AL1507065 | 20 | 100/5 | 228.8667 | 229.0098 | 227.7171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
91 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756SAB | SABJI MANDI_26154422756SMD | Agriculture | Near Khushi traders | 63 | AL1507066 | 20 | 100/5 | 223.4877 | 220.3777 | 220.8299 | 0 | 0 | 15.4 | 0.77 | 5.1333 | 0 | 0 | 3.4008 | 3.4008 | 200 | Critical | 5.4 | Normal
92 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756SAB | SABJI MANDI_26154422756SMD | Agriculture | IN FRONT OF INDIAN OVERSEAS BANK | 100 | AL1507067 | 40 | 200/5 | 225.8834 | 0 | 0 | 117.2 | 135.2 | 66 | 1.5546 | 106.1333 | 26.4735 | 0 | 0 | 26.4735 | 27.39 | Critical | 26.47 | Normal
93 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Rajkumar ke ghar ke pass nagla Buddha dt19 | 25 | AL1507071 | 10 | 50/5 | 193.6017 | 189.4266 | 190.5614 | 0 | 10 | 0 | 1 | 3.3333 | 0 | 1.8943 | 0 | 1.8943 | 200 | Critical | 7.58 | Normal
94 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Nahar pr midakhur | 100 | AL1507073 | 40 | 200/5 | 183.2358 | 183.6266 | 183.9374 | 44 | 59.6 | 136 | 2.1319 | 79.8667 | 8.0624 | 10.9441 | 25.0155 | 44.022 | 70.28 | Critical | 44.02 | Normal
95 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Thakr nohavatSingh schooldt18 | 25 | AL1507074 | 10 | 50/5 | 183.93 | 0 | 181.4626 | 37.5 | 0 | 0 | 3.75 | 12.5 | 6.8974 | 0 | 0 | 6.8974 | 200 | Critical | 27.59 | Normal
96 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Gdi daulta jatav basti | 100 | AL1507075 | 40 | 200/5 | 161.1461 | 177.4212 | 8.3686 | 0 | 129.6 | 8 | 3.1448 | 45.8667 | 0 | 22.9938 | 0.066949 | 23.0607 | 182.56 | Critical | 23.06 | Normal
97 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Airtel tower sakatpur dt05 | 25 | AL1507077 | 10 | 50/5 | 198.5329 | 195.2557 | 196.1689 | 0 | 15.8 | 0.1 | 1.575 | 5.3 | 0 | 3.085 | 0.019617 | 3.1047 | 198.11 | Critical | 12.42 | Normal
98 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Sony Ram master ke ghar ke pass sakatpur dt07 | 10 | AL1507078 | 10 | 50/5 | 187.5551 | 196.1286 | 196.5653 | 58.7 | 45.4 | 41.4 | 1.5687 | 48.5 | 11.0095 | 8.9042 | 8.1378 | 28.0515 | 21.03 | Critical | 280.52 | Critical
99 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Nagla Buddha first dt17 | 63 | AL1507079 | 10 | 50/5 | 193.4198 | 190.747 | 194.7341 | 29 | 0.1 | 25 | 2.7122 | 18.0333 | 5.6092 | 0.019075 | 4.8684 | 10.4966 | 60.81 | Critical | 16.66 | Normal
100 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Baroda mandir ke pass DT11 | 25 | AL1507081 | 10 | 50/5 | 194.4684 | 193.4424 | 188.9999 | 49 | 0 | 0 | 4.9 | 16.3333 | 9.529 | 0 | 0 | 9.529 | 200 | Critical | 38.12 | Normal
101 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Adity petrol pump dt37 | 25 | AL1507082 | 10 | 50/5 | 182.0787 | 0 | 8.412 | 31.4 | 29.9 | 0 | 3.0678 | 20.4333 | 5.7173 | 0 | 0 | 5.7173 | 53.67 | Critical | 22.87 | Normal
102 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Petrol pump baroda DT09 | 63 | AL1507084 | 10 | 50/5 | 195.1741 | 193.294 | 193.7316 | 14.7 | 25.2 | 27.4 | 1.1755 | 22.4333 | 2.8691 | 4.871 | 5.3082 | 13.0483 | 22.14 | Critical | 20.71 | Normal
103 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Baba mohan das ke samne | 25 | AL1507087 | 10 | 50/5 | 193.1019 | 193.4323 | 196.6318 | 79.5 | 0 | 0 | 7.95 | 26.5 | 15.3516 | 0 | 0 | 15.3516 | 200 | Critical | 61.41 | Normal
104 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Dev hotal DT06 | 25 | AL1507088 | 10 | 50/5 | 197.027 | 197.3405 | 47.4544 | 35.6 | 27.1 | 54.7 | 2.4483 | 39.1333 | 7.0142 | 5.3479 | 2.5958 | 14.9578 | 39.78 | Critical | 59.83 | Normal
105 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Korai 1st | 250 | AL1507089 | 40 | 200/5 | 187.1299 | 187.8073 | 191.3752 | 0 | 2 | 0 | 0.05 | 0.66667 | 0 | 0.37561 | 0 | 0.37561 | 200 | Critical | 0.15 | Normal
106 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Jal Nigam korai petrol pump ke pass | 25 | AL1507090 | 10 | 50/5 | 178.0708 | 178.6211 | 179.6615 | 49.4 | 18.8 | 19.5 | 3.0256 | 29.2333 | 8.7967 | 3.3581 | 3.5034 | 15.6582 | 68.99 | Critical | 62.63 | Normal
107 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Ekta city dt13 | 16 | AL1507091 | 10 | 50/5 | 228.1476 | 231.4827 | 229.5932 | 0 | 1.4 | 0.1 | 0.13528 | 0.5 | 0 | 0.32408 | 0.022959 | 0.34704 | 180 | Critical | 2.17 | Normal
108 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Siva balagi dt07 | 10 | AL1507094 | 10 | 50/5 | 223.0893 | 11.6054 | 0 | 20.1 | 22.1 | 0 | 2.1171 | 14.0667 | 4.4841 | 0.25648 | 0 | 4.7406 | 57.11 | Critical | 47.41 | Normal
109 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Bus stop kriaoli | 16 | AL1507096 | 40 | 200/5 | 228.3005 | 222.9385 | 222.1346 | 64 | 169.2 | 42 | 2.9438 | 91.7333 | 14.6112 | 37.7212 | 9.3297 | 61.6621 | 84.45 | Critical | 385.39 | Critical
110 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463DOOR | DOORA_26154434463DOR | Agriculture | Dura raod mandir ke pass | 10 | AL1507099 | 20 | 100/5 | 0 | 183.5679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
111 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACN | ACHHNERA TOWN NO-2_26154412016AC2 | Agriculture | Kachora road Kamal colony 2 | 100 | AL1507100 | 40 | 200/5 | 218.425 | 216.6849 | 18.7126 | 62 | 117.2 | 76 | 1.2425 | 85.0667 | 13.5424 | 25.3955 | 1.4222 | 40.36 | 37.77 | Critical | 40.36 | Normal
112 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Reliance petrol pump kirabwli | 63 | AL1507681 | 10 | 50/5 | 195.3135 | 192.9538 | 199.7263 | 0 | 23.1 | 0.1 | 2.305 | 7.7333 | 0 | 4.4572 | 0.019973 | 4.4772 | 198.71 | Critical | 7.11 | Normal
113 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Ballo ki fectroy | 63 | AL1507682 | 10 | 50/5 | 226.752 | 225.1497 | 225.2325 | 11.4 | 17.1 | 9.3 | 0.69907 | 12.6 | 2.585 | 3.8501 | 2.0947 | 8.5297 | 35.71 | Critical | 13.54 | Normal
114 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Chaudhary vikram singh cold dt14 | 315 | AL1507684 | 20 | 100/5 | 212.9431 | 204.9574 | 210.406 | 15 | 8.8 | 12.2 | 0.26889 | 12 | 3.1941 | 1.8036 | 2.567 | 7.5647 | 25 | Critical | 2.4 | Normal
115 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Parmhunsh aasharm satha | 100 | AL1507686 | 40 | 200/5 | 194.304 | 1.2067 | 2.1501 | 6 | 8 | 69.6 | 1.5656 | 27.8667 | 1.1658 | 0.0096533 | 0.14965 | 1.3251 | 149.76 | Critical | 1.33 | Normal
116 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Sujan singh market dabwali raod | 16 | AL1507687 | 10 | 50/5 | 199.4576 | 199.0812 | 200.0276 | 0 | 39.2 | 1.3 | 3.8566 | 13.5 | 0 | 7.804 | 0.26004 | 8.064 | 190.37 | Critical | 50.4 | Normal
117 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Nagla todu | 100 | AL1507690 | 40 | 200/5 | 1.1149 | 188.2156 | 189.2623 | 96 | 69.6 | 42 | 1.1692 | 69.2 | 0.10703 | 13.0998 | 7.949 | 21.1559 | 38.73 | Critical | 21.16 | Normal
118 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | BSNL TOWER | 25 | AL1507691 | 80 | 400/5 | 223.9701 | 223.1562 | 226.0308 | 186.4 | 219.2 | 288.8 | 1.1321 | 231.4667 | 41.748 | 48.9158 | 65.2777 | 155.9415 | 24.77 | Critical | 623.77 | Critical
119 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Basant Bihar colony | 100 | AL1507692 | 40 | 200/5 | 223.8547 | 228.4239 | 221.6567 | 180.8 | 74.4 | 0 | 3.9348 | 85.0667 | 40.4729 | 16.9947 | 0 | 57.4677 | 112.54 | Critical | 57.47 | Normal
120 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Dangal ground | 100 | AL1507694 | 40 | 200/5 | 221.5126 | 226.3127 | 219.2169 | 99.6 | 0 | 64.4 | 2.1871 | 54.6667 | 22.0627 | 0 | 14.1176 | 36.1802 | 82.2 | Critical | 36.18 | Normal
121 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Basant vihar kriaoli | 100 | AL1507697 | 40 | 200/5 | 222.3419 | 223.5252 | 217.3071 | 70.4 | 90.4 | 63.2 | 0.61025 | 74.6667 | 15.6529 | 20.2067 | 13.7338 | 49.5934 | 21.07 | Critical | 49.59 | Normal
122 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | HDFC bank kriaoli | 63 | AL1507698 | 20 | 100/5 | 224.9566 | 225.8854 | 228.0959 | 9 | 4.6 | 10.8 | 0.27622 | 8.1333 | 2.0246 | 1.0391 | 2.4634 | 5.5271 | 32.79 | Critical | 8.77 | Normal
123 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | Gam se bahar dt12 | 63 | AL1507704 | 10 | 50/5 | 192.0687 | 196.051 | 185.1148 | 45 | 8.3 | 37.5 | 3.3584 | 30.2667 | 8.6431 | 1.6272 | 6.9418 | 17.2121 | 48.68 | Critical | 27.32 | Normal
124 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Bijli ghr ke pss 1st | 25 | AL1507711 | 10 | 50/5 | 97.9423 | 200.1894 | 198.3996 | 0 | 0.2 | 43.8 | 4.37 | 14.6667 | 0 | 0.040038 | 8.6899 | 8.7299 | 198.64 | Critical | 34.92 | Normal
125 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Railway station road mdakhur | 25 | AL1507716 | 10 | 50/5 | 203.2335 | 196.6109 | 191.0682 | 6.9 | 51.3 | 17.4 | 4.0192 | 25.2 | 1.4023 | 10.0861 | 3.3246 | 14.813 | 103.57 | Critical | 59.25 | Normal
126 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Nayara petrol pump | 25 | AL1507717 | 10 | 50/5 | 203.3868 | 201.2252 | 202.4975 | 16.8 | 48.4 | 8.1 | 3.6731 | 24.4333 | 3.4169 | 9.7393 | 1.6402 | 14.7964 | 98.09 | Critical | 59.19 | Normal
127 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Gokul restaurant | 10 | AL1507718 | 10 | 50/5 | 199.5691 | 200.4734 | 198.8381 | 8.4 | 0 | 0 | 0.84 | 2.8 | 1.6764 | 0 | 0 | 1.6764 | 200 | Critical | 16.76 | Normal
128 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Tata ka tawer midakhur | 25 | AL1507722 | 10 | 50/5 | 201.7568 | 198.9871 | 202.1767 | 13.9 | 23 | 0.2 | 1.9879 | 12.3667 | 2.8044 | 4.5767 | 0.040435 | 7.4216 | 85.98 | Critical | 29.69 | Normal
129 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Jatav basti dabli DT37 | 100 | AL1507723 | 40 | 200/5 | 187.8875 | 186.3999 | 184.7161 | 67.6 | 130 | 244 | 3.8733 | 147.2 | 12.7012 | 24.232 | 45.0707 | 82.0039 | 65.76 | Critical | 82 | Warning
130 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Shmashan Ghat ke pass davaliDT18 | 25 | AL1507724 | 10 | 50/5 | 185.7522 | 0 | 185.9879 | 25.4 | 0 | 0 | 2.54 | 8.4667 | 4.7181 | 0 | 0 | 4.7181 | 200 | Critical | 18.87 | Normal
131 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DBI | DABALI_26154424669DBI | Agriculture | Dawali fauji market pss DT40 | 100 | AL1507725 | 10 | 50/5 | 194.6085 | 197.3406 | 198.8472 | 45.7 | 16.7 | 0 | 4.0052 | 20.8 | 8.8936 | 3.2956 | 0 | 12.1892 | 119.71 | Critical | 12.19 | Normal
132 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Railway station midakhur | 25 | AL1507726 | 10 | 50/5 | 195.6754 | 200.2147 | 200.4884 | 29 | 54.6 | 31.2 | 2.4574 | 38.2667 | 5.6746 | 10.9317 | 6.2552 | 22.8615 | 42.68 | Critical | 91.45 | Critical
133 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669PAI | PALI_26154424669PAL | Agriculture | BSNL tower Pali dt08 | 25 | AL1507729 | 10 | 50/5 | 146.8002 | 189.665 | 190.4694 | 0 | 15.7 | 32.9 | 2.8502 | 16.2 | 0 | 2.9777 | 6.2664 | 9.2442 | 103.09 | Critical | 36.98 | Normal
134 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | BSNL TOWER MIDAKUR | 25 | AL1507730 | 10 | 50/5 | 0.94156 | 201.1589 | 192.8631 | 15 | 25.4 | 0 | 2.2117 | 13.4667 | 0.014123 | 5.1094 | 0 | 5.1236 | 88.61 | Critical | 20.49 | Normal
135 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | N S COld store DT01 | 400 | AL1507732 | 80 | 400/5 | 175.5393 | 177.6365 | 179.5672 | 227.2 | 206.4 | 131.2 | 1.0934 | 188.2667 | 39.8825 | 36.6642 | 23.5592 | 100.1059 | 20.68 | Critical | 25.03 | Normal
136 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Sigarpur 2nd samudayik sauchalay | 100 | AL1507734 | 40 | 200/5 | 156.6791 | 176.8514 | 178.1564 | 196.8 | 134.8 | 136 | 1.5352 | 155.8667 | 30.8345 | 23.8396 | 24.2293 | 78.9033 | 26.26 | Critical | 78.9 | Normal
137 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Malikpur first | 100 | AL1507735 | 40 | 200/5 | 0.06713 | 174.9407 | 175.6425 | 169.6 | 92.8 | 134.8 | 1.6652 | 132.4 | 0.011385 | 16.2345 | 23.6766 | 39.9225 | 28.1 | Critical | 39.92 | Normal
138 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Moni dham colony kriaoli | 100 | AL1508263 | 40 | 200/5 | 222.4537 | 224.6574 | 223.4529 | 179.2 | 156 | 242.4 | 1.9363 | 192.5333 | 39.8637 | 35.0466 | 54.165 | 129.0752 | 25.9 | Critical | 129.08 | Critical
139 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756SAB | SABJI MANDI_26154422756SMD | Agriculture | Maruti Suzuki motors Ke Samne | 25 | AL1508264 | 10 | 50/5 | 53.9475 | 229.6432 | 242.602 | 0 | 96.2 | 32.2 | 8.4815 | 42.8 | 0 | 22.0917 | 7.8118 | 29.9035 | 124.77 | Critical | 119.61 | Critical
140 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DRE | DREAM CITY_26154424669DRM | Agriculture | DREAM CITY-4 | 250 | AL1508561 | 80 | 400/5 | 246.1283 | 246.8008 | 245.6302 | 64.8 | 156 | 38.4 | 1.3359 | 86.4 | 15.9491 | 38.5009 | 9.4322 | 63.8822 | 80.56 | Critical | 25.55 | Normal
141 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DRE | DREAM CITY_26154424669DRM | Agriculture | DREAM CITY -1 | 250 | AL1508562 | 80 | 400/5 | 244.9681 | 248.4154 | 245.3332 | 79.2 | 42.4 | 116 | 0.79674 | 79.2 | 19.4015 | 10.5328 | 28.4586 | 58.3929 | 46.46 | Critical | 23.36 | Normal
142 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DRE | DREAM CITY_26154424669DRM | Agriculture | DREAM CITY-3 | 250 | AL1508564 | 80 | 400/5 | 246.4841 | 245.1073 | 242.6777 | 0 | 165.6 | 60.8 | 1.8136 | 75.4667 | 0 | 40.5898 | 14.7548 | 55.3446 | 119.43 | Critical | 22.14 | Normal
143 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DRE | DREAM CITY_26154424669DRM | Agriculture | DREAM CITY-6 | 250 | AL1508565 | 80 | 400/5 | 246.0842 | 246.7256 | 245.2376 | 66.4 | 160.8 | 112 | 1.0221 | 113.0667 | 16.34 | 39.6735 | 27.4666 | 83.4801 | 42.22 | Critical | 33.39 | Normal
144 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Nagla Mansa 1st dt05 | 25 | AL1508567 | 10 | 50/5 | 172.1168 | 179.0522 | 181.5697 | 49 | 7.6 | 3.5 | 4.3595 | 20.0333 | 8.4337 | 1.3608 | 0.63549 | 10.43 | 144.59 | Critical | 41.72 | Normal
145 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Nagla saliga 2th | 10 | AL1508569 | 10 | 50/5 | 167.0236 | 158.8483 | 66.3195 | 20.5 | 0 | 0 | 2.05 | 6.8333 | 3.424 | 0 | 0 | 3.424 | 200 | Critical | 34.24 | Normal
146 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACN | ACHHNERA TOWN NO-2_26154412016AC2 | Agriculture | Airtel tawer dt36 | 25 | AL1508570 | 10 | 50/5 | 218.6538 | 220.7864 | 225.69 | 17.6 | 39 | 19.1 | 2.0691 | 25.2333 | 3.8483 | 8.6107 | 4.3107 | 16.7697 | 54.56 | Critical | 67.08 | Normal
147 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | Can vibhag kriaoli | 250 | AL1508574 | 80 | 400/5 | 223.3025 | 226.8413 | 228.1889 | 282.4 | 178.4 | 0.8 | 3.0829 | 153.8667 | 63.0606 | 40.4685 | 0.18255 | 103.7117 | 83.54 | Critical | 41.48 | Normal
148 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Near by kriaoli tahsil | 250 | AL1508575 | 40 | 200/5 | 210.1714 | 214.1885 | 213.9832 | 0.4 | 118 | 123.2 | 3.0071 | 80.5333 | 0.084069 | 25.2742 | 26.3627 | 51.721 | 52.98 | Critical | 20.69 | Normal
149 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | Shashank Agrawal factory | 25 | AL1508577 | 10 | 50/5 | 225.2545 | 0 | 9.6401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
150 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669DRE | DREAM CITY_26154424669DRM | Agriculture | DREAM CITY-5 | 250 | AL1508578 | 80 | 400/5 | 245.9838 | 247.4491 | 245.5763 | 40 | 97.6 | 64.8 | 0.62554 | 67.4667 | 9.8394 | 24.151 | 15.9133 | 49.9037 | 44.66 | Critical | 19.96 | Normal
151 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | Prakash Colony | 100 | AL1508579 | 20 | 100/5 | 225.9988 | 224.9507 | 218.8055 | 27 | 3.4 | 72.4 | 3.0371 | 34.2667 | 6.102 | 0.76483 | 15.8415 | 22.7083 | 111.28 | Critical | 22.71 | Normal
152 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Airtel tower korai | 25 | AL1508581 | 10 | 50/5 | 229.3187 | 223.7618 | 227.7258 | 5.1 | 26.8 | 11.6 | 1.929 | 14.5 | 1.1695 | 5.9968 | 2.6416 | 9.808 | 84.83 | Critical | 39.23 | Normal
153 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACN | ACHHNERA TOWN NO-2_26154412016AC2 | Agriculture | Cinema hol achhnera | 100 | AL1508583 | 40 | 200/5 | 225.327 | 225.145 | 225.654 | 68 | 122.4 | 61.2 | 1.4525 | 83.8667 | 15.3222 | 27.5578 | 13.81 | 56.69 | 45.95 | Critical | 56.69 | Normal
154 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | Jio tawar dt35 | 25 | AL1508584 | 10 | 50/5 | 222.4262 | 222.0568 | 221.1981 | 27 | 1.5 | 19.3 | 2.2654 | 15.9333 | 6.0055 | 0.33309 | 4.2691 | 10.6077 | 69.46 | Critical | 42.43 | Normal
155 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | Near bus stand dt01 | 100 | AL1508585 | 40 | 200/5 | 218.2414 | 218.8266 | 222.4471 | 18 | 43.2 | 46.8 | 0.67949 | 36 | 3.9283 | 9.4533 | 10.4105 | 23.7922 | 30 | Critical | 23.79 | Normal
156 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACN | ACHHNERA TOWN NO-2_26154412016AC2 | Agriculture | Gulab nagar 2nd | 100 | AL1508588 | 40 | 200/5 | 225.1621 | 226.6063 | 224.6341 | 68 | 0.4 | 79.6 | 1.8521 | 49.3333 | 15.311 | 0.090643 | 17.8809 | 33.2825 | 61.35 | Critical | 33.28 | Normal
157 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | MIDHAKUR | 26154424669MID | MIDAKUR_26154424669MDP | Agriculture | Bijli ghar Pokhar ke paas1 | 100 | AL1508589 | 40 | 200/5 | 33.8395 | 204.1297 | 201.7777 | 78.8 | 0.4 | 10.8 | 1.8438 | 30 | 2.6666 | 0.081652 | 2.1792 | 4.9274 | 162.67 | Critical | 4.93 | Normal
158 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Jio tower korai | 25 | AL1508590 | 10 | 50/5 | 195.78 | 193.6967 | 192.9404 | 7.5 | 11.4 | 25.1 | 1.601 | 14.6667 | 1.4683 | 2.2081 | 4.8428 | 8.5193 | 71.14 | Critical | 34.08 | Normal
159 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | Jal nigam kriaoli | 25 | AL1508591 | 10 | 50/5 | 221.9816 | 221.8208 | 210.4764 | 53.5 | 29.4 | 0 | 4.6408 | 27.6333 | 11.876 | 6.5215 | 0 | 18.3975 | 93.61 | Critical | 73.59 | Normal
160 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | Kana residency | 63 | AL1508592 | 20 | 100/5 | 221.1877 | 224.5327 | 224.2141 | 114.4 | 36 | 0 | 5.0658 | 50.1333 | 25.3039 | 8.0832 | 0 | 33.3871 | 128.19 | Critical | 53 | Normal
161 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756MON | MONI ASHRAM DHAM_26154422756MBA | Agriculture | Runkta moad jal nigam | 25 | AL1508594 | 40 | 200/5 | 219.7055 | 222.5871 | 226.4875 | 34.4 | 34.4 | 59.6 | 0.63 | 42.8 | 7.5579 | 7.657 | 13.4987 | 28.7135 | 39.25 | Critical | 114.85 | Critical
162 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | BSNL tawer | 25 | AL1508595 | 40 | 200/5 | 223.9805 | 220.1896 | 221.1887 | 68 | 0 | 62.8 | 1.6389 | 43.6 | 15.2307 | 0 | 13.8906 | 29.1213 | 55.96 | Critical | 116.49 | Critical
163 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | 33/11 KV KIRAWALI(IPDS) | 26154412756ABH | ABHUAPURA_26154422756ABP | Agriculture | Lakshmi gardan | 63 | AL1508597 | 10 | 50/5 | 228.3222 | 227.3802 | 230.8229 | 8.8 | 15.4 | 9.3 | 0.63647 | 11.1667 | 2.0092 | 3.5017 | 2.1467 | 7.6575 | 37.91 | Critical | 12.15 | Normal
164 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACN | ACHHNERA TOWN NO-2_26154412016AC2 | Agriculture | Kashi ram 2nd colony | 100 | AL1508602 | 40 | 200/5 | 219.6452 | 214.6822 | 217.0578 | 30.4 | 89.6 | 82 | 1.3947 | 67.3333 | 6.6772 | 19.2355 | 17.7987 | 43.7115 | 33.07 | Critical | 43.71 | Normal
165 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | Jal nigham dt15 | 25 | AL1508604 | 10 | 50/5 | 219.3407 | 220.5838 | 220.9796 | 4.7 | 20.4 | 22.1 | 1.6615 | 15.7333 | 1.0309 | 4.4999 | 4.8836 | 10.4145 | 40.47 | Critical | 41.66 | Normal
166 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | Jio tawar dt25 | 25 | AL1508605 | 10 | 50/5 | 223.2117 | 222.8034 | 0 | 0 | 26.3 | 27.5 | 2.692 | 17.9333 | 0 | 5.8597 | 0 | 5.8597 | 53.35 | Critical | 23.44 | Normal
167 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | Balaji traders ke samane dt18 | 100 | AL1508607 | 40 | 200/5 | 224.1469 | 224.2408 | 221.1241 | 31.2 | 20 | 101.6 | 1.9154 | 50.9333 | 6.9934 | 4.4848 | 22.4662 | 33.9444 | 99.48 | Critical | 33.94 | Normal
168 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIRA | KIRAWALI-2_26154424596KW2 | Agriculture | Nagla hatti | 100 | AL1508609 | 40 | 200/5 | 188.6584 | 192.461 | 187.867 | 36.4 | 96 | 80.8 | 1.341 | 71.0667 | 6.8672 | 18.4763 | 15.1797 | 40.5231 | 35.08 | Critical | 40.52 | Normal
169 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | Pm Shri pradhikaran vidhyalaya 2nd dt 34 | 100 | AL1508610 | 40 | 200/5 | 2.6354 | 221.9573 | 224.7221 | 118 | 77.6 | 1.2 | 2.5685 | 65.6 | 0.31098 | 17.2239 | 0.26967 | 17.8045 | 79.88 | Critical | 17.8 | Normal
170 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855AKB | AKHBAI RURAL | Agriculture | Ramkishor ki chakki akhvayi DT08 | 25 | AL1514861 | 10 | 50/5 | 182.7695 | 181.2802 | 180.9221 | 15.3 | 6.9 | 15 | 0.82541 | 12.4 | 2.7964 | 1.2508 | 2.7138 | 6.761 | 23.39 | Critical | 27.04 | Normal
171 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Nagla banjra DT01 | 25 | AL1514863 | 20 | 100/5 | 221.1152 | 176.9207 | 315.9347 | 0 | 103.6 | 0 | 5.18 | 34.5333 | 0 | 18.329 | 0 | 18.329 | 200 | Critical | 73.32 | Normal
172 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Tajpur 1 | 25 | AL1514867 | 10 | 50/5 | 180.3746 | 180.9011 | 174.4456 | 0 | 0 | 69.8 | 6.98 | 23.2667 | 0 | 0 | 12.1763 | 12.1763 | 200 | Critical | 48.71 | Normal
173 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Kirrya mandir ke paas dt10 | 25 | AL1514869 | 10 | 50/5 | 169.078 | 172.4022 | 168.018 | 14.6 | 0.2 | 30.8 | 2.6516 | 15.2 | 2.4685 | 0.03448 | 5.175 | 7.678 | 102.63 | Critical | 30.71 | Normal
174 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Jal nigam nagla jhariya DT31 | 25 | AL1514944 | 0 | 100/5 | 168.4436 | 174.1581 | 178.5643 | 0 | 1.51 | 4.77 | 4.2226 | 2.0933 | 0 | 0.26298 | 0.85175 | 1.1147 | 127.87 | Critical | 4.46 | Normal
175 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RUA | RURAL-2_26154412016RL2 | Agriculture | Swasthya Kendra Arua Khas ke samne dt02 | 25 | AL1514961 | 10 | 50/5 | 166.2235 | 167.9945 | 167.7352 | 70.2 | 11.7 | 47 | 5.1022 | 42.9667 | 11.6689 | 1.9655 | 7.8836 | 21.518 | 63.38 | Critical | 86.07 | Warning
176 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Nahar ke pass byara DT30 | 25 | AL1514962 | 10 | 50/5 | 162.8466 | 0 | 156.1676 | 17.5 | 0 | 43.3 | 3.7728 | 20.2667 | 2.8498 | 0 | 6.7621 | 9.6119 | 113.65 | Critical | 38.45 | Normal
177 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Jio tower byara DT29 | 25 | AL1514967 | 10 | 50/5 | 0 | 172.8047 | 154.3279 | 17 | 40.5 | 17.5 | 2.3254 | 25 | 0 | 6.9986 | 2.7007 | 9.6993 | 62 | Critical | 38.8 | Normal
178 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RUA | RURAL-2_26154412016RL2 | Agriculture | BSNL tower rabha | 25 | AL1514969 | 10 | 50/5 | 167.4466 | 169.4696 | 169.5475 | 12.6 | 30.9 | 26.2 | 1.6461 | 23.2333 | 2.1098 | 5.2366 | 4.4421 | 11.7886 | 33 | Critical | 47.15 | Normal
179 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RUA | RURAL-2_26154412016RL2 | Agriculture | Jio tawer dt06 | 25 | AL1514970 | 10 | 50/5 | 174.6575 | 171.4905 | 173.9168 | 11.9 | 25.6 | 12.4 | 1.3457 | 16.6333 | 2.0784 | 4.3902 | 2.1566 | 8.6252 | 53.91 | Critical | 34.5 | Normal
180 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Pura vale byara DT27 | 100 | AL1514979 | 40 | 200/5 | 157.0039 | 158.4161 | 164.48 | 171.2 | 163.6 | 80 | 2.1912 | 138.2667 | 26.8791 | 25.9169 | 13.1584 | 65.9543 | 23.82 | Critical | 65.95 | Normal
181 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888DAU | DAULTABAD_26154414888DLB | Agriculture | Pokar ke pass baseri road nyabas dt07 | 63 | AL1518196 | 20 | 100/5 | 185.019 | 183.2316 | 180.8425 | 52.6 | 72.6 | 86.8 | 1.488 | 70.6667 | 9.732 | 13.3026 | 15.6971 | 38.7317 | 22.83 | Critical | 61.48 | Normal
182 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Byara ghdi raod DT16 | 25 | AL1518216 | 10 | 50/5 | 172.0955 | 162.4219 | 21.6877 | 17.8 | 76.2 | 0 | 6.9043 | 31.3333 | 3.0633 | 12.3766 | 0 | 15.4399 | 143.19 | Critical | 61.76 | Normal
183 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Jaatav pokhar ke pass | 100 | AL1518220 | 40 | 200/5 | 158.7364 | 161.8987 | 154.1504 | 96 | 92 | 172.8 | 1.9719 | 120.2667 | 15.2387 | 14.8947 | 26.6372 | 56.7706 | 43.68 | Critical | 56.77 | Normal
184 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Byara daulat pani plant DT26 | 100 | AL1518381 | 40 | 200/5 | 155.2008 | 154.3988 | 8.7748 | 149.2 | 79.2 | 136.8 | 1.6174 | 121.7333 | 23.156 | 12.2284 | 1.2004 | 36.5847 | 22.56 | Critical | 36.58 | Normal
185 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RUA | RURAL-2_26154412016RL2 | Agriculture | Adde per kalicharn ke ghar ke paas magrool jaat dt10 | 25 | AL1518385 | 10 | 50/5 | 94.9075 | 157.5181 | 168.3262 | 6 | 70.4 | 0 | 6.76 | 25.4667 | 0.56945 | 11.0893 | 0 | 11.6587 | 176.44 | Critical | 46.63 | Normal
186 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Kailasi ki aata chakki ke pass | 100 | AL1518390 | 40 | 200/5 | 129.052 | 114.1849 | 139.0347 | 170 | 106 | 261.2 | 3.3773 | 179.0667 | 21.9388 | 12.1036 | 36.3159 | 70.3583 | 45.87 | Critical | 70.36 | Normal
187 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359KAC | KACHAURA_26154414560KCR | Agriculture | VIJAY KE GHR KE SAMNE | 25 | AL1518493 | 10 | 50/5 | 171.8753 | 114.5726 | 124.6001 | 47.8 | 0 | 0 | 4.78 | 15.9333 | 8.2156 | 0 | 0 | 8.2156 | 200 | Critical | 32.86 | Normal
188 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Kirrya school ke anddr DT09 | 100 | AL1518603 | 40 | 200/5 | 151.0441 | 5.8796 | 0.87256 | 11.6 | 0 | 11.6 | 0.29 | 7.7333 | 1.7521 | 0 | 0.010122 | 1.7622 | 50 | Critical | 1.76 | Normal
189 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Nagriya mandir ke pass DT05 | 100 | AL1518609 | 40 | 200/5 | 19.1314 | 174.3289 | 174.06 | 92.8 | 96.4 | 0.8 | 2.3463 | 63.3333 | 1.7754 | 16.8053 | 0.13925 | 18.7199 | 52.21 | Critical | 18.72 | Normal
190 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Sonu ki chaki ke paas dt12 | 25 | AL1518642 | 10 | 50/5 | 171.06 | 163.0562 | 168.4978 | 0 | 70.3 | 25.8 | 6.1595 | 32.0333 | 0 | 11.4628 | 4.3472 | 15.8101 | 119.46 | Critical | 63.24 | Normal
191 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RUA | RURAL-2_26154412016RL2 | Agriculture | Indus Tower Mangrol Jaat dt11 | 25 | AL1518643 | 10 | 50/5 | 169.9348 | 168.6025 | 166.1571 | 15.8 | 28.3 | 37 | 1.8458 | 27.0333 | 2.685 | 4.7715 | 6.1478 | 13.6042 | 36.87 | Critical | 54.42 | Normal
192 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Kirrya samar1 dt08 | 25 | AL1518650 | 10 | 50/5 | 162.896 | 24.3607 | 168.3486 | 74.4 | 99.9 | 20.3 | 7.0403 | 64.8667 | 12.1195 | 2.4336 | 3.4175 | 17.9706 | 54.01 | Critical | 71.88 | Normal
193 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Nagla banjara DT11 | 100 | AL1518736 | 40 | 200/5 | 49.438 | 171.1248 | 165.9692 | 98.4 | 12.4 | 44 | 1.8836 | 51.6 | 4.8647 | 2.1219 | 7.3026 | 14.2893 | 90.7 | Critical | 14.29 | Normal
194 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888DAU | DAULTABAD_26154414888DLB | Agriculture | nale ke pass daulatabad Dt01 | 25 | AL1518985 | 10 | 50/5 | 199.0376 | 0 | 0 | 27.1 | 0 | 0 | 2.71 | 9.0333 | 5.3939 | 0 | 0 | 5.3939 | 200 | Critical | 21.58 | Normal
195 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888DAU | DAULTABAD_26154414888DLB | Agriculture | Rajkumar ke ghar ke pass daulatabad dt03 | 25 | AL1518986 | 10 | 50/5 | 187.8135 | 182.6445 | 186.5455 | 1.4 | 34.8 | 12.6 | 2.9444 | 16.2667 | 0.26294 | 6.356 | 2.3505 | 8.9694 | 113.93 | Critical | 35.88 | Normal
196 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Arera 4th DT22 | 63 | AL1523111 | 20 | 100/5 | 159.2064 | 164.8898 | 171.4932 | 79.8 | 30.4 | 17.2 | 2.8577 | 42.4667 | 12.7047 | 5.0126 | 2.9497 | 20.667 | 87.91 | Critical | 32.8 | Normal
197 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | GANPATI RESORT PAR | 63 | AL1523114 | 20 | 100/5 | 195.3532 | 194.2319 | 196.8677 | 65.2 | 77.6 | 37.4 | 1.7828 | 60.0667 | 12.737 | 15.0724 | 7.3629 | 35.1723 | 29.19 | Critical | 55.83 | Normal
198 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Nagla ramli 1 | 63 | AL1523119 | 20 | 100/5 | 182.1141 | 184.0498 | 179.4149 | 87.4 | 34.8 | 109.4 | 3.3196 | 77.2 | 15.9168 | 6.4049 | 19.628 | 41.9497 | 41.71 | Critical | 66.59 | Normal
199 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | Primary school ke pass | 63 | AL1523120 | 20 | 100/5 | 191.3098 | 193.9377 | 191.7149 | 26 | 51.4 | 0.2 | 2.217 | 25.8667 | 4.9741 | 9.9684 | 0.038343 | 14.9808 | 98.71 | Critical | 23.78 | Normal
200 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RAB | RAYBHA_26154412016RAY | Agriculture | Kaila Devi feeling station pump | 25 | AL1523141 | 10 | 50/5 | 183.56 | 190.2079 | 188.099 | 26.8 | 3.3 | 18.8 | 2.0694 | 16.3 | 4.9194 | 0.62769 | 3.5363 | 9.0834 | 64.42 | Critical | 36.33 | Normal
201 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RAB | RAYBHA_26154412016RAY | Agriculture | Katwai Road Talab ke pass raiba dt20 | 25 | AL1523142 | 10 | 50/5 | 177.2165 | 180.4001 | 178.62 | 89.5 | 34.5 | 77.9 | 5.0215 | 67.3 | 15.8609 | 6.2238 | 13.9145 | 35.9992 | 32.99 | Critical | 144 | Critical
202 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RAB | RAYBHA_26154412016RAY | Agriculture | UP ITI College dhanauli road rabha | 25 | AL1523144 | 10 | 50/5 | 186.5409 | 185.2968 | 184.6555 | 0 | 6.7 | 0 | 0.67 | 2.2333 | 0 | 1.2415 | 0 | 1.2415 | 200 | Critical | 4.97 | Normal
203 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RAB | RAYBHA_26154412016RAY | Agriculture | Jio tawer dt08 | 25 | AL1523145 | 10 | 50/5 | 183.6839 | 188.1562 | 187.2914 | 28.4 | 0 | 8.3 | 2.5293 | 12.2333 | 5.2166 | 0 | 1.5545 | 6.7711 | 132.15 | Critical | 27.08 | Normal
204 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Prachin hanuman mandir garhima | 100 | AL1523150 | 40 | 200/5 | 172.0399 | 170.4966 | 170.8065 | 119.2 | 15.6 | 111.2 | 2.496 | 82 | 20.5072 | 2.6597 | 18.9937 | 42.1606 | 45.37 | Critical | 42.16 | Normal
205 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RAB | RAYBHA_26154412016RAY | Agriculture | BSNL TOWER DT19 | 25 | AL1523151 | 10 | 50/5 | 195.8391 | 194.0018 | 192.9307 | 0 | 0.1 | 32.6 | 3.255 | 10.9 | 0 | 0.0194 | 6.2895 | 6.3089 | 199.08 | Critical | 25.24 | Normal
206 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RAB | RAYBHA_26154412016RAY | Agriculture | Indus Tower dt26 | 25 | AL1523154 | 10 | 50/5 | 183.4462 | 183.7693 | 181.1317 | 12.9 | 12.8 | 28 | 1.515 | 17.9 | 2.3665 | 2.3522 | 5.0717 | 9.7904 | 56.42 | Critical | 39.16 | Normal
207 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Mai airtel tower DT09 | 25 | AL1523157 | 10 | 50/5 | 187.1778 | 185.2472 | 185.9072 | 26 | 25.1 | 12.8 | 1.2774 | 21.3 | 4.8666 | 4.6497 | 2.3796 | 11.8959 | 22.07 | Critical | 47.58 | Normal
208 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809FTP | FATEHPURA_26154414809FTP | Agriculture | Shiv mandir sandhan | 25 | AL1523159 | 10 | 50/5 | 0 | 186.3951 | 177.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
209 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | (Bhadkaul) DTR 04 | 250 | AL1523167 | 80 | 400/5 | 194.6754 | 186.2853 | 193.5168 | 264 | 238.4 | 156 | 1.2218 | 219.4667 | 51.3943 | 44.4104 | 30.1886 | 125.9934 | 20.29 | Critical | 50.4 | Normal
210 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Mai near by airtel tower DT10 | 100 | AL1523182 | 40 | 200/5 | 184.6622 | 182.2329 | 183.775 | 85.2 | 180 | 122.4 | 2.0683 | 129.2 | 15.7332 | 32.8019 | 22.4941 | 71.0292 | 39.32 | Critical | 71.03 | Normal
211 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635GOT | GOTHRA_26154414635GTR | Agriculture | Nagla mandoli DT04 | 63 | AL1523187 | 40 | 200/5 | 177.2347 | 176.9638 | 17.817 | 57.2 | 116 | 137.2 | 1.7947 | 103.4667 | 10.1378 | 20.5278 | 2.4445 | 33.1101 | 32.6 | Critical | 52.56 | Normal
212 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Primary school ke pass a1 | 100 | AL1523188 | 40 | 200/5 | 185.9984 | 186.1073 | 106.2524 | 301.2 | 202 | 130.4 | 3.714 | 211.2 | 56.0227 | 37.5937 | 13.8553 | 107.4717 | 42.61 | Critical | 107.47 | Critical
213 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Nahchani udayvir dudiya ke ghr ke pas DT24 | 63 | AL1523190 | 20 | 100/5 | 182.8936 | 185.1464 | 183.8415 | 45.4 | 18.4 | 33.8 | 1.173 | 32.5333 | 8.3034 | 3.4067 | 6.2138 | 17.9239 | 39.55 | Critical | 28.45 | Normal
214 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | GANDHI SMARAK INTER COLLEGE | 25 | AL1523233 | 10 | 50/5 | 159.58 | 173.8876 | 173.343 | 64.6 | 14.7 | 36.1 | 4.336 | 38.4667 | 10.3089 | 2.5561 | 6.2577 | 19.1227 | 67.94 | Critical | 76.49 | Normal
215 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | PETROL PUMP PAR | 25 | AL1523234 | 10 | 50/5 | 174.1099 | 177.0608 | 179.4832 | 0 | 14.3 | 0 | 1.43 | 4.7667 | 0 | 2.532 | 0 | 2.532 | 200 | Critical | 10.13 | Normal
216 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | Jio tower silmbad DT04 | 25 | AL1523235 | 10 | 50/5 | 190.3112 | 191.6671 | 192.4047 | 19.1 | 0 | 4.9 | 1.7182 | 8 | 3.6349 | 0 | 0.94278 | 4.5777 | 138.75 | Critical | 18.31 | Normal
217 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | Indus tower par | 25 | AL1523236 | 10 | 50/5 | 190.0655 | 184.884 | 191.0206 | 0.4 | 0.1 | 0.1 | 0.03 | 0.2 | 0.076026 | 0.018488 | 0.019102 | 0.11362 | 100 | Critical | 0.45 | Normal
218 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | Bhavanpura 1st gao me ghuste hi DT05 | 25 | AL1523237 | 10 | 50/5 | 187.1125 | 185.0483 | 187.27 | 66.5 | 96.1 | 45.3 | 4.4194 | 69.3 | 12.443 | 17.7831 | 8.4833 | 38.7095 | 38.67 | Critical | 154.84 | Critical
219 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | Rakhi chahar petrol pump DT16 | 25 | AL1523239 | 10 | 50/5 | 192.4249 | 187.7461 | 191.32 | 0 | 27.7 | 0 | 2.77 | 9.2333 | 0 | 5.2006 | 0 | 5.2006 | 200 | Critical | 20.8 | Normal
220 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809SDN.. | SADHAN_26154414809SDN... | Agriculture | Sadhan sarkari hospital 1st DT09 | 100 | AL1523242 | 40 | 200/5 | 175.5672 | 179.0807 | 178.7759 | 197.6 | 143.2 | 228 | 1.8603 | 189.6 | 34.6921 | 25.6444 | 40.7609 | 101.0973 | 20.25 | Critical | 101.1 | Critical
221 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635TUR | TURKIYA_26154414635TRK | Agriculture | Petha factory turkiya nehar ke pass | 25 | AL1523243 | 10 | 50/5 | 0 | 166.5057 | 121.5612 | 3.3 | 29.4 | 0 | 2.7897 | 10.9 | 0 | 4.8953 | 0 | 4.8953 | 169.72 | Critical | 19.58 | Normal
222 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Poultry farm ke pass | 25 | AL1523245 | 10 | 50/5 | 184.2043 | 186.2368 | 185.7301 | 39.8 | 27.8 | 26.8 | 1.253 | 31.4667 | 7.3313 | 5.1774 | 4.9776 | 17.4863 | 26.48 | Critical | 69.95 | Normal
223 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Bada mandir mai | 63 | AL1523248 | 10 | 50/5 | 200.1784 | 194.6831 | 198.4629 | 17.5 | 68 | 0 | 6.1158 | 28.5 | 3.5031 | 13.2384 | 0 | 16.7416 | 138.6 | Critical | 26.57 | Normal
224 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | New hanuman mandir ke pass | 25 | AL1523249 | 10 | 50/5 | 188.3631 | 172.8554 | 183.4091 | 0 | 0 | 40.3 | 4.03 | 13.4333 | 0 | 0 | 7.3914 | 7.3914 | 200 | Critical | 29.57 | Normal
225 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Janutha keetham road kachaura | 25 | AL1523250 | 10 | 50/5 | 184.3525 | 186.4369 | 181.6902 | 26.3 | 0 | 82.9 | 7.3375 | 36.4 | 4.8485 | 0 | 15.0621 | 19.9106 | 127.75 | Critical | 79.64 | Normal
226 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Sarkari tnki jariya nagla DT27 | 25 | AL1523252 | 10 | 50/5 | 171.9494 | 166.0946 | 166.3629 | 14.5 | 42.7 | 38.4 | 2.6315 | 31.8667 | 2.4933 | 7.0922 | 6.3883 | 15.9738 | 34 | Critical | 63.9 | Normal
227 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Kabristan ke pass gobara | 63 | AL1523254 | 20 | 100/5 | 167.29 | 167.9835 | 162.1581 | 192.8 | 0.2 | 179.8 | 9.322 | 124.2667 | 32.2535 | 0.033597 | 29.156 | 61.4431 | 55.15 | Critical | 97.53 | Critical
228 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Bhadiri adda DT18 | 25 | AL1523255 | 10 | 50/5 | 0 | 162.3784 | 163.129 | 0 | 59.2 | 18.4 | 5.2478 | 25.8667 | 0 | 9.6128 | 3.0016 | 12.6144 | 128.87 | Critical | 50.46 | Normal
229 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809FTP | FATEHPURA_26154414809FTP | Agriculture | Fatehpura shera vali devi mandir DT09 | 25 | AL1523258 | 10 | 50/5 | 177.9901 | 178.7318 | 182.4301 | 56.1 | 37.1 | 0.1 | 4.9325 | 31.1 | 9.9852 | 6.631 | 0.018243 | 16.6344 | 80.39 | Critical | 66.54 | Normal
230 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Nagla Banjara saray 2nd DT 10 | 25 | AL1523284 | 10 | 50/5 | 175.9281 | 172.2701 | 175.1077 | 17.1 | 39.8 | 41.7 | 2.3707 | 32.8667 | 3.0084 | 6.8563 | 7.302 | 17.1667 | 26.88 | Critical | 68.67 | Normal
231 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Davar godam ke pass DT 18 | 25 | AL1523285 | 10 | 50/5 | 180.0933 | 177.2232 | 177.9351 | 0 | 18.5 | 25.4 | 2.2749 | 14.6333 | 0 | 3.2786 | 4.5196 | 7.7982 | 73.58 | Critical | 31.19 | Normal
232 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654MGK | MANGOLI KALA_26154434654MGK | Agriculture | Suresh pandit ji ka khet mangoli khurd | 100 | AL1523286 | 40 | 200/5 | 174.5401 | 170.1888 | 174.3977 | 121.2 | 184 | 124.8 | 1.527 | 143.3333 | 21.1543 | 31.3147 | 21.7648 | 74.2338 | 28.37 | Critical | 74.23 | Normal
233 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654AUL | AULENDA_26154434654AUL | Agriculture | Nagla haribhkchh DT 14 | 100 | AL1523287 | 40 | 200/5 | 55.6205 | 153.5084 | 161.1175 | 0.4 | 77.2 | 42 | 1.6647 | 39.8667 | 0.022248 | 11.8508 | 6.7669 | 18.64 | 93.65 | Critical | 18.64 | Normal
234 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Jio tower dabar | 25 | AL1523288 | 10 | 50/5 | 86.1569 | 0 | 148.6898 | 23 | 0 | 23.6 | 2.3306 | 15.5333 | 1.9816 | 0 | 3.5091 | 5.4907 | 51.93 | Critical | 21.96 | Normal
235 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Samra prathmik health center DT14 | 25 | AL1523289 | 10 | 50/5 | 190.0251 | 186.9323 | 183.5758 | 0 | 0 | 26.9 | 2.69 | 8.9667 | 0 | 0 | 4.9382 | 4.9382 | 200 | Critical | 19.75 | Normal
236 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Talab ke pass dabar d1 | 25 | AL1523290 | 10 | 50/5 | 184.6398 | 171.114 | 175.949 | 20 | 98.9 | 91.9 | 7.5643 | 70.2667 | 3.6928 | 16.9232 | 16.1697 | 36.7857 | 40.75 | Critical | 147.14 | Critical
237 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Nahachani gyani medical store DT23 | 100 | AL1523511 | 40 | 200/5 | 188.2599 | 176.461 | 184.9843 | 62.8 | 161.6 | 20.4 | 3.1373 | 81.6 | 11.8227 | 28.5161 | 3.7737 | 44.1125 | 98.04 | Critical | 44.11 | Normal
238 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | Chahar baseri samsan ghat DT08 | 25 | AL1523512 | 10 | 50/5 | 4.461e-05 | 178.2595 | 98.3298 | 21.3 | 73 | 85.4 | 5.8887 | 59.9 | 9.5019e-07 | 13.0129 | 8.3974 | 21.4103 | 42.57 | Critical | 85.64 | Warning
239 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MUBARAKPUR | 22001432508CHI | CHAI POKHAR_26154414677CPK | Agriculture | Airtel tower chai pokhar DT29 | 25 | AL1523517 | 10 | 50/5 | 150.3956 | 150.0593 | 176.2699 | 24.9 | 12.2 | 46.1 | 2.9664 | 27.7333 | 3.7449 | 1.8307 | 8.126 | 13.7016 | 66.23 | Critical | 54.81 | Normal
240 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MUBARAKPUR | 22001432508CHI | CHAI POKHAR_26154414677CPK | Agriculture | VEERANGNA AWANTI BAAI SCHOOL KE SAMNE | 100 | AL1523519 | 40 | 200/5 | 145.7476 | 28.8379 | 160.1586 | 150 | 246.4 | 136 | 2.6027 | 177.4667 | 21.8621 | 7.1056 | 21.7816 | 50.7494 | 38.84 | Critical | 50.75 | Normal
241 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | SAMUDAYIK SOCHALYA KE SAMNE 1 | 100 | AL1523520 | 40 | 200/5 | 172.9341 | 171.5606 | 112.43 | 0 | 210.8 | 248.4 | 5.7974 | 153.0667 | 0 | 36.165 | 27.9276 | 64.0926 | 62.28 | Critical | 64.09 | Normal
242 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | Lohiya aavas colony | 250 | AL1523533 | 80 | 400/5 | 235.0292 | 231.4154 | 229.3321 | 8.8 | 87.2 | 1.6 | 1.028 | 32.5333 | 2.0683 | 20.1794 | 0.36693 | 22.6146 | 168.03 | Critical | 9.05 | Normal
243 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855AKB | AKHBAI RURAL | Agriculture | DHARAM SINGH KE MAKAN KE PASS | 63 | AL1523535 | 20 | 100/5 | 179.9627 | 180.6859 | 182.3558 | 0 | 89.8 | 0 | 4.49 | 29.9333 | 0 | 16.2256 | 0 | 16.2256 | 200 | Critical | 25.75 | Normal
244 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Panchayat ghar ke pass | 250 | AL1523536 | 80 | 400/5 | 182.4373 | 186.2346 | 184.3421 | 286.4 | 369.6 | 255.2 | 1.2804 | 303.7333 | 52.2501 | 68.8323 | 47.0441 | 168.1264 | 21.69 | Critical | 67.25 | Normal
245 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Bala g properties | 250 | AL1523537 | 80 | 400/5 | 207.1558 | 205.2319 | 205.5893 | 2.4 | 10.4 | 0 | 0.1179 | 4.2667 | 0.49717 | 2.1344 | 0 | 2.6316 | 143.75 | Critical | 1.05 | Normal
246 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | INDRA SCHOOL KE PASS 2 | 100 | AL1523539 | 40 | 200/5 | 228.5499 | 229.843 | 227.7522 | 3.2 | 0 | 3.2 | 0.08 | 2.1333 | 0.73136 | 0 | 0.72881 | 1.4602 | 50 | Critical | 1.46 | Normal
247 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 22001432016RAB | RAYBHA_26154412016RAY | Agriculture | Jal Nigam1 dt10 | 25 | AL1523546 | 10 | 50/5 | 180.4263 | 184.9903 | 184.2558 | 23 | 0 | 0 | 2.3 | 7.6667 | 4.1498 | 0 | 0 | 4.1498 | 200 | Critical | 16.6 | Normal
248 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Prathmik vidyalaya ke pass | 100 | AL1523547 | 40 | 200/5 | 115.8896 | 1.1685 | 141.7068 | 257.2 | 268 | 23.6 | 5.9796 | 182.9333 | 29.8068 | 0.31317 | 3.3443 | 33.4643 | 46.5 | Critical | 33.46 | Normal
249 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Primary school ke pass tripura DT20 | 63 | AL1523548 | 40 | 200/5 | 161.6405 | 0 | 150.0288 | 68.4 | 0 | 228 | 5.0663 | 98.8 | 11.0562 | 0 | 34.2066 | 45.2628 | 130.77 | Critical | 71.85 | Normal
250 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Rakesh pandit ke plot ke pass | 100 | AL1523549 | 40 | 200/5 | 168.4771 | 171.6048 | 85.0555 | 74.4 | 32 | 180 | 3.3002 | 95.4667 | 12.5347 | 5.4914 | 15.31 | 33.336 | 88.55 | Critical | 33.34 | Normal
251 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809FTP | FATEHPURA_26154414809FTP | Agriculture | Talab ke pass khera sandhan 2 | 100 | AL1523553 | 40 | 200/5 | 178.4027 | 179.368 | 177.5053 | 0 | 101.6 | 86.4 | 2.3729 | 62.6667 | 0 | 18.2238 | 15.3365 | 33.5602 | 62.13 | Critical | 33.56 | Normal
252 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809FTP | FATEHPURA_26154414809FTP | Agriculture | Talab ke pass sandhan khera | 100 | AL1523555 | 40 | 200/5 | 186.7671 | 166.5605 | 178.8536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
253 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809SDN.. | SADHAN_26154414809SDN... | Agriculture | Sadhan saver vala DT04 | 100 | AL1523556 | 40 | 200/5 | 135.6906 | 128.1359 | 62.3154 | 122 | 72.8 | 98.4 | 1.0655 | 97.7333 | 16.5543 | 9.3283 | 6.1318 | 32.0144 | 24.83 | Critical | 32.01 | Normal
254 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809FTP | FATEHPURA_26154414809FTP | Agriculture | Prathmik vidyalaya ke samne | 100 | AL1523557 | 40 | 200/5 | 182.2784 | 182.8401 | 181.9452 | 142.8 | 50.4 | 102.8 | 2.0065 | 98.6667 | 26.0294 | 9.2151 | 18.704 | 53.9485 | 44.73 | Critical | 53.95 | Normal
255 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Nawab ke plot ke pass nagla kachaura | 100 | AL1523558 | 40 | 200/5 | 174.7913 | 176.8689 | 159.0572 | 85.6 | 105.2 | 128.4 | 0.92774 | 106.4 | 14.9621 | 18.6066 | 20.4229 | 53.9917 | 20.68 | Critical | 53.99 | Normal
256 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809SDN.. | SADHAN_26154414809SDN... | Agriculture | Kalua thakur ke ghar ke pass | 100 | AL1523559 | 40 | 200/5 | 77.798 | 85.8783 | 88.2445 | 400 | 102.4 | 6.4 | 8.8865 | 169.6 | 31.1192 | 8.7939 | 0.56476 | 40.4779 | 135.85 | Critical | 40.48 | Normal
257 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Podina ke khet ke pass gobara | 100 | AL1523581 | 40 | 200/5 | 172.982 | 166.3283 | 164.7655 | 10 | 106 | 110.4 | 2.4568 | 75.4667 | 1.7298 | 17.6308 | 18.1901 | 37.5507 | 46.29 | Critical | 37.55 | Normal
258 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Bastai baliya ke khet pr DT04 | 25 | AL1523615 | 10 | 50/5 | 189.2068 | 177.2328 | 184.9926 | 0 | 79.4 | 29.9 | 6.9457 | 36.4333 | 0 | 14.0723 | 5.5313 | 19.6036 | 117.93 | Critical | 78.41 | Normal
259 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359KAC | KACHAURA_26154414560KCR | Agriculture | ACHHNERA ITI | 25 | AL1523617 | 10 | 50/5 | 194.5672 | 193.0991 | 196.2486 | 0 | 0 | 6.9 | 0.69 | 2.3 | 0 | 0 | 1.3541 | 1.3541 | 200 | Critical | 5.42 | Normal
260 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635GOT | GOTHRA_26154414635GTR | Agriculture | Mandoli 2nd DT02 | 25 | AL1523641 | 10 | 50/5 | 172.4848 | 170.726 | 174.7493 | 80.3 | 8.5 | 0.1 | 7.6347 | 29.6333 | 13.8505 | 1.4512 | 0.017475 | 15.3192 | 170.98 | Critical | 61.28 | Normal
261 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | Beman india tower DT15 | 25 | AL1523645 | 10 | 50/5 | 178.9519 | 177.3197 | 184.0057 | 39.3 | 35.5 | 19.9 | 1.7807 | 31.5667 | 7.0328 | 6.2949 | 3.6617 | 16.9894 | 24.5 | Critical | 67.96 | Normal
262 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635GOT | GOTHRA_26154414635GTR | Agriculture | Gothra panchayat ghr ke pass DT08 | 100 | AL1523647 | 40 | 200/5 | 176.0317 | 0 | 81.7218 | 108.4 | 291.2 | 173.2 | 4.0132 | 190.9333 | 19.0818 | 0 | 14.1542 | 33.2361 | 52.51 | Critical | 33.24 | Normal
263 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635TUR | TURKIYA_26154414635TRK | Agriculture | Primary school jharothi | 25 | AL1523648 | 10 | 50/5 | 146.6159 | 146.503 | 173.3841 | 0 | 0 | 22.1 | 2.21 | 7.3667 | 0 | 0 | 3.8318 | 3.8318 | 200 | Critical | 15.33 | Normal
264 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | Jindpura jio tower 24 | 25 | AL1523649 | 10 | 50/5 | 186.9435 | 184.8103 | 187.5775 | 16.1 | 33.1 | 0 | 2.8669 | 16.4 | 3.0098 | 6.1172 | 0 | 9.127 | 101.83 | Critical | 36.51 | Normal
265 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | Pokhar ke pass | 100 | AL1523651 | 40 | 200/5 | 172.5332 | 59.8263 | 20.8001 | 176 | 117.2 | 32.4 | 3.126 | 108.5333 | 30.3658 | 7.0116 | 0.67392 | 38.0514 | 62.16 | Critical | 38.05 | Normal
266 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MUBARAKPUR | 22001432508CHI | CHAI POKHAR_26154414677CPK | Agriculture | Kisni ke ghr pr achhnera raod DT36 | 25 | AL1523652 | 10 | 50/5 | 0 | 173.8179 | 109.0246 | 0 | 34.2 | 0 | 3.42 | 11.4 | 0 | 5.9446 | 0 | 5.9446 | 200 | Critical | 23.78 | Normal
267 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MUBARAKPUR | 22001432508CHI | CHAI POKHAR_26154414677CPK | Agriculture | PADMA KE KHET PAR | 63 | AL1523653 | 20 | 100/5 | 182.8164 | 129.261 | 72.2468 | 125.6 | 61.2 | 57.4 | 3.3191 | 81.4 | 22.9617 | 7.9108 | 4.147 | 35.0195 | 54.3 | Critical | 55.59 | Normal
268 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | Chekora primary school ke pass DT22 | 63 | AL1523654 | 20 | 100/5 | 0 | 188.0733 | 185.3551 | 0 | 110 | 90.8 | 5.0884 | 66.9333 | 0 | 20.6881 | 16.8302 | 37.5183 | 64.34 | Critical | 59.55 | Normal
269 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | LAVANIYA KHAAD BEEJ BHANDAR | 63 | AL1523655 | 20 | 100/5 | 186.5505 | 183.4588 | 188.616 | 65.6 | 138.6 | 28 | 4.8702 | 77.4 | 12.2377 | 25.4274 | 5.2812 | 42.9464 | 79.07 | Critical | 68.17 | Normal
270 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | Baseri chahr gao me ghuste hi DT03 | 25 | AL1523656 | 10 | 50/5 | 177.3798 | 175.8278 | 181.1517 | 64.3 | 97.6 | 42.3 | 4.8223 | 68.0667 | 11.4055 | 17.1608 | 7.6627 | 36.229 | 43.39 | Critical | 144.92 | Critical
271 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MUBARAKPUR | 22001432508BAB | BABROD_26154414677BBD | Agriculture | Babrod jio tower DT01 | 25 | AL1523657 | 10 | 50/5 | 181.0182 | 181.0768 | 180.3287 | 23.1 | 23 | 11.5 | 1.155 | 19.2 | 4.1815 | 4.1648 | 2.0738 | 10.4201 | 20.31 | Critical | 41.68 | Normal
272 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | Jegara panchayat ghr ke pass DT18 | 63 | AL1523658 | 20 | 100/5 | 179.0505 | 176.3982 | 174.7648 | 0 | 81.6 | 108.6 | 4.8966 | 63.4 | 0 | 14.3941 | 18.9795 | 33.3735 | 71.29 | Critical | 52.97 | Normal
273 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | SALEMABAD VILLAGE END POINT | 25 | AL1523659 | 20 | 100/5 | 190.8168 | 186.5071 | 185.9513 | 27.6 | 74.8 | 114 | 3.7466 | 72.1333 | 5.2665 | 13.9507 | 21.1985 | 40.4157 | 58.04 | Critical | 161.66 | Critical
274 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Nagla bich durgesh ki dukan ke pass DT07 | 100 | AL1523660 | 40 | 200/5 | 138.8685 | 185.9935 | 179.7968 | 90 | 184 | 122 | 2.0694 | 132 | 12.4982 | 34.2228 | 21.9352 | 68.6562 | 39.39 | Critical | 68.66 | Normal
275 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635TUR | TURKIYA_26154414635TRK | Agriculture | Turkiya 2nd DT07 | 25 | AL1523664 | 10 | 50/5 | 171.4075 | 171.0002 | 164.9916 | 87.1 | 58.1 | 0.1 | 7.6727 | 48.4333 | 14.9296 | 9.9351 | 0.016499 | 24.8812 | 79.83 | Critical | 99.52 | Critical
276 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Jio tower daru ka theka DT 01 | 25 | AL1523685 | 10 | 50/5 | 171.566 | 177.1418 | 174.6825 | 19.2 | 17.3 | 0.3 | 1.8025 | 12.2667 | 3.2941 | 3.0646 | 0.052405 | 6.411 | 56.52 | Critical | 25.64 | Normal
277 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855AKB | AKHBAI RURAL | Agriculture | Indust tower nagla bhagat DT15 | 25 | AL1523686 | 10 | 50/5 | 177.5815 | 179.8803 | 180.4104 | 37.7 | 20.3 | 20.5 | 1.7301 | 26.1667 | 6.6948 | 3.6516 | 3.6984 | 14.0448 | 44.08 | Critical | 56.18 | Normal
278 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Nagla jabba bhabo ke ghr ke picce DT17 | 25 | AL1523687 | 10 | 50/5 | 177.4477 | 181.7699 | 180.7848 | 76.5 | 47.1 | 55.9 | 2.6136 | 59.8333 | 13.5747 | 8.5614 | 10.1059 | 32.242 | 27.86 | Critical | 128.97 | Critical
279 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Near by airtel tower DT13 | 63 | AL1523689 | 20 | 100/5 | 177.9469 | 186.4454 | 186.5135 | 105.4 | 67.2 | 70.2 | 1.8396 | 80.9333 | 18.7556 | 12.5291 | 13.0932 | 44.378 | 30.23 | Critical | 70.44 | Normal
280 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Rajkiy pashu Kendra dawar dt06 | 25 | AL1523692 | 10 | 50/5 | 173.4762 | 174.1519 | 176.2751 | 9.3 | 0 | 0 | 0.93 | 3.1 | 1.6133 | 0 | 0 | 1.6133 | 200 | Critical | 6.45 | Normal
281 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Ayushman Arogya mandir doora | 25 | AL1523693 | 10 | 50/5 | 157.7597 | 73.1439 | 157.5251 | 4.6 | 0 | 0 | 0.46 | 1.5333 | 0.72569 | 0 | 0 | 0.72569 | 200 | Critical | 2.9 | Normal
282 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654AUL | AULENDA_26154434654AUL | Agriculture | Nagla mth 1st DT 04 | 25 | AL1523694 | 10 | 50/5 | 65.4278 | 170.5415 | 114.2776 | 0 | 38.9 | 0 | 3.89 | 12.9667 | 0 | 6.6341 | 0 | 6.6341 | 200 | Critical | 26.54 | Normal
283 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Samra jio tower DT03 | 25 | AL1523696 | 10 | 50/5 | 179.4971 | 179.3529 | 183.5032 | 19.9 | 15.5 | 0 | 1.8106 | 11.8 | 3.572 | 2.78 | 0 | 6.352 | 68.64 | Critical | 25.41 | Normal
284 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Arera jio tower DT24 | 25 | AL1523697 | 10 | 50/5 | 162.1674 | 164.0511 | 169.1796 | 24.6 | 0 | 0 | 2.46 | 8.2 | 3.9893 | 0 | 0 | 3.9893 | 200 | Critical | 15.96 | Normal
285 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Jio tower tikri DT 05 | 25 | AL1523698 | 10 | 50/5 | 158.6068 | 166.1051 | 165.9338 | 0 | 0 | 49 | 4.9 | 16.3333 | 0 | 0 | 8.1308 | 8.1308 | 200 | Critical | 32.52 | Normal
286 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Shri pitamber dham mandir deoretha | 25 | AL1523699 | 10 | 50/5 | 95.1843 | 0.72209 | 164.5793 | 0 | 0 | 0.5 | 0.05 | 0.16667 | 0 | 0 | 0.08229 | 0.08229 | 200 | Critical | 0.33 | Normal
287 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654AUL | AULENDA_26154434654AUL | Agriculture | Nagla dyonari 2nd DT28 | 25 | AL1523901 | 10 | 50/5 | 181.4511 | 176.4555 | 181.0529 | 14.9 | 88.6 | 22.9 | 7.0043 | 42.1333 | 2.7036 | 15.634 | 4.1461 | 22.4837 | 110.28 | Critical | 89.93 | Warning
288 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Krishna khad beej Bhandar samra | 63 | AL1523903 | 20 | 100/5 | 180.6289 | 185.3882 | 185.1756 | 101.8 | 54.4 | 27.2 | 3.2695 | 61.1333 | 18.388 | 10.0851 | 5.0368 | 33.5099 | 66.52 | Critical | 53.19 | Normal
289 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654AUL | AULENDA_26154434654AUL | Agriculture | Nagla faram 2nd DT26 | 25 | AL1523905 | 10 | 50/5 | 177.9627 | 173.7459 | 174.7433 | 25.8 | 61.2 | 14.2 | 4.2407 | 33.7333 | 4.5914 | 10.6332 | 2.4814 | 17.706 | 81.42 | Critical | 70.82 | Normal
290 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855JYT | JYOTIRAJ_26154424855JTR | Agriculture | Jyotiraj amit ke ghr ke pass DT02 | 63 | AL1523906 | 20 | 100/5 | 187.188 | 183.9676 | 188.6363 | 84 | 95.4 | 49 | 2.094 | 76.1333 | 15.7238 | 17.5505 | 9.2432 | 42.5175 | 25.31 | Critical | 67.49 | Normal
291 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654AUL | AULENDA_26154434654AUL | Agriculture | Nagla jagge 1st DT 15 | 100 | AL1523909 | 40 | 200/5 | 0 | 173.3792 | 172.3428 | 0 | 35.2 | 82.4 | 1.7903 | 39.2 | 0 | 6.1029 | 14.201 | 20.304 | 110.2 | Critical | 20.3 | Normal
292 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654AUL | AULENDA_26154434654AUL | Agriculture | Nagla dharam 3rd DT 09 | 25 | AL1523910 | 10 | 50/5 | 180.0073 | 181.2119 | 181.6984 | 13.6 | 9 | 8.5 | 0.48693 | 10.3667 | 2.4481 | 1.6309 | 1.5444 | 5.6234 | 31.19 | Critical | 22.49 | Normal
293 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | Vamanpura 2nd panchayat ghe ke pas DT07 | 63 | AL1523911 | 20 | 100/5 | 187.3945 | 189.1841 | 187.0139 | 0 | 0 | 64.8 | 3.24 | 21.6 | 0 | 0 | 12.1185 | 12.1185 | 200 | Critical | 19.24 | Normal
294 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | OM SHANTI MARRIAGE HOME KE PASS | 25 | AL1523912 | 20 | 100/5 | 227.9323 | 178.5262 | 180.9425 | 28.8 | 14.8 | 18.4 | 0.6296 | 20.6667 | 6.5645 | 2.6422 | 3.3293 | 12.536 | 39.35 | Critical | 50.14 | Normal
295 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Om shiv shakti building meterial ke pass | 63 | AL1523913 | 20 | 100/5 | 186.2032 | 187.0387 | 188.7992 | 0 | 51.4 | 0 | 2.57 | 17.1333 | 0 | 9.6138 | 0 | 9.6138 | 200 | Critical | 15.26 | Normal
296 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | Jengara indus tower DT28 | 25 | AL1523914 | 10 | 50/5 | 180.8987 | 182.345 | 171.2173 | 41.6 | 0 | 43.1 | 4.237 | 28.2333 | 7.5254 | 0 | 7.3795 | 14.9049 | 52.66 | Critical | 59.62 | Normal
297 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | NAHAR PAR MANDIR KE PASS | 63 | AL1523915 | 20 | 100/5 | 179.7365 | 177.1257 | 179.6142 | 113.2 | 56.4 | 0 | 4.9017 | 56.5333 | 20.3462 | 9.9899 | 0 | 30.3361 | 100.24 | Critical | 48.15 | Normal
298 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | Jengara BSNL tower DT27 | 25 | AL1523916 | 10 | 50/5 | 183.3473 | 183.9859 | 183.2457 | 3.6 | 15.9 | 18.7 | 1.3913 | 12.7333 | 0.66005 | 2.9254 | 3.4267 | 7.0121 | 46.86 | Critical | 28.05 | Normal
299 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533CHE | CHEKORA_26154424533CKR | Agriculture | BHAWAN PURA VILLAGE ME | 25 | AL1523919 | 10 | 50/5 | 190.452 | 189.3045 | 185.5403 | 18.2 | 35.9 | 47 | 2.5159 | 33.7 | 3.4662 | 6.796 | 8.7204 | 18.9827 | 39.47 | Critical | 75.93 | Normal
300 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533BAS | BASERI CHAHAR_26154424533BSC | Agriculture | Beman mulayam singh ke ghr ke pass DT16 | 25 | AL1523920 | 10 | 50/5 | 172.8817 | 185.0989 | 181.3489 | 62.7 | 0 | 14.5 | 5.6854 | 25.7333 | 10.8397 | 0 | 2.6296 | 13.4692 | 143.65 | Critical | 53.88 | Normal
301 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809FTP | FATEHPURA_26154414809FTP | Agriculture | Basiya rajpoot school ke pass DT01 | 63 | AL1523932 | 20 | 100/5 | 183.3585 | 176.9433 | 174.869 | 81.2 | 81.2 | 120.2 | 1.95 | 94.2 | 14.8887 | 14.3678 | 21.0193 | 50.2758 | 27.6 | Critical | 79.8 | Normal
302 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Chirmoli tuhiram ki dukan ke pass DT03 | 250 | AL1523934 | 80 | 400/5 | 179.7831 | 186.3017 | 183.8315 | 374.4 | 212 | 291.2 | 1.7582 | 292.5333 | 67.3108 | 39.496 | 53.5317 | 160.3385 | 27.99 | Critical | 64.14 | Normal
303 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Hasela bade talab ke pass | 100 | AL1523936 | 40 | 200/5 | 174.2622 | 168.966 | 170.0395 | 51.6 | 43.2 | 88 | 1.0312 | 60.9333 | 8.9919 | 7.2993 | 14.9635 | 31.2547 | 44.42 | Critical | 31.25 | Normal
304 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809GBR | GOBARA_26154414809GBR | Agriculture | Bhadiri talab ke pass 2 | 63 | AL1523939 | 20 | 100/5 | 0 | 143.3135 | 146.6035 | 0 | 35.6 | 46.8 | 2.1163 | 27.4667 | 0 | 5.102 | 6.861 | 11.963 | 70.39 | Critical | 18.99 | Normal
305 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809SDN.. | SADHAN_26154414809SDN... | Agriculture | Prem Chand baghel ke ghar ke samne | 63 | AL1523940 | 20 | 100/5 | 176.4242 | 178.7784 | 178.4553 | 161 | 93.2 | 119.2 | 2.9623 | 124.4667 | 28.4043 | 16.6621 | 21.2719 | 66.3383 | 29.35 | Critical | 105.3 | Critical
306 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809SDN.. | SADHAN_26154414809SDN... | Agriculture | Esak ke ghar ke pass | 25 | AL1523944 | 10 | 50/5 | 174.7899 | 168.8099 | 0 | 58.6 | 94.5 | 0 | 8.2623 | 51.0333 | 10.2427 | 15.9525 | 0 | 26.1952 | 85.17 | Critical | 104.78 | Critical
307 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635GOT | GOTHRA_26154414635GTR | Agriculture | Pandit mandoli mandir ke pas DT03 | 63 | AL1523951 | 20 | 100/5 | 151.149 | 191.1671 | 181.7644 | 0 | 46.4 | 55.2 | 2.5684 | 33.8667 | 0 | 8.8702 | 10.0334 | 18.9035 | 62.99 | Critical | 30.01 | Normal
308 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Nanau mandir ke pass gao me ghuste hi DT14 | 63 | AL1523954 | 20 | 100/5 | 189.0048 | 184.1887 | 187.497 | 28 | 64 | 42.6 | 1.5681 | 44.8667 | 5.2921 | 11.7881 | 7.9874 | 25.0676 | 42.64 | Critical | 39.79 | Normal
309 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MUBARAKPUR | 22001432508CHI | CHAI POKHAR_26154414677CPK | Agriculture | CHAPOKHR ME POKHAR KE PASS | 63 | AL1523955 | 20 | 100/5 | 178.1685 | 179.0361 | 172.1054 | 21 | 0 | 133 | 6.1921 | 51.3333 | 3.7415 | 0 | 22.89 | 26.6316 | 159.09 | Critical | 42.27 | Normal
310 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | SADHAN | 26154414809FTP | FATEHPURA_26154414809FTP | Agriculture | Fatehpura jugendra | 63 | AL1523957 | 20 | 100/5 | 180.4503 | 182.1767 | 179.9574 | 74.6 | 0 | 149.6 | 6.4779 | 74.7333 | 13.4616 | 0 | 26.9216 | 40.3832 | 100.18 | Critical | 64.1 | Normal
311 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | MANDOLI | 22001434635TUR | TURKIYA_26154414635TRK | Agriculture | Turkiya moksh dham | 63 | AL1523958 | 20 | 100/5 | 0 | 161.4136 | 0 | 128.6 | 67.6 | 194 | 5.4744 | 130.0667 | 0 | 10.9116 | 0 | 10.9116 | 49.15 | Critical | 17.32 | Normal
312 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | KACHAURA | 22001432359MAI | MAI_26154414560MAI | Agriculture | Nanau primary school ke pass DT13 | 63 | AL1523959 | 20 | 100/5 | 187.8544 | 182.3547 | 186.9237 | 2.6 | 63 | 31.2 | 2.6166 | 32.2667 | 0.48842 | 11.4883 | 5.832 | 17.8088 | 95.25 | Critical | 28.27 | Normal
313 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Chandrahans ke plot ke pass | 100 | AL1531902 | 40 | 200/5 | 178.9794 | 179.8213 | 184.2553 | 128.8 | 152.8 | 48.4 | 2.3677 | 110 | 23.0526 | 27.4767 | 8.918 | 59.4472 | 38.91 | Critical | 59.45 | Normal
314 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Sikrauda1 | 100 | AL1531903 | 40 | 200/5 | 159.7083 | 161.2505 | 48.5087 | 126 | 123.2 | 56 | 1.7161 | 101.7333 | 20.1232 | 19.8661 | 2.7165 | 42.7058 | 23.85 | Critical | 42.71 | Normal
315 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Nagla param sukh a1 | 100 | AL1531906 | 40 | 200/5 | 160.1385 | 156.9388 | 0 | 127.6 | 151.6 | 83.2 | 1.5027 | 120.8 | 20.4337 | 23.7919 | 0 | 44.2256 | 25.5 | Critical | 44.23 | Normal
316 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Tikari pokhar ke pas DT 07 | 100 | AL1531908 | 40 | 200/5 | 172.1558 | 169.6364 | 169.8404 | 64.4 | 112 | 68.4 | 1.1433 | 81.6 | 11.0868 | 18.9993 | 11.6171 | 41.7032 | 37.25 | Critical | 41.7 | Normal
317 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Nagla har govind d1 | 100 | AL1531909 | 40 | 200/5 | 162.2661 | 163.3416 | 163.1135 | 149.6 | 92 | 25.6 | 2.6869 | 89.0667 | 24.275 | 15.0274 | 4.1757 | 43.4781 | 67.96 | Critical | 43.48 | Normal
318 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Nagla banjara saray 1st DT 09 | 63 | AL1531911 | 40 | 200/5 | 179.4959 | 178.5386 | 179.523 | 98 | 126.8 | 152 | 1.17 | 125.6 | 17.5906 | 22.6387 | 27.2875 | 67.5168 | 21.02 | Critical | 107.17 | Critical
319 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Ganga prasad ji ke ghar ke pass nagla ramle | 100 | AL1531912 | 40 | 200/5 | 183.5409 | 23.305 | 70.1116 | 103.2 | 122 | 64.8 | 1.2624 | 96.6667 | 18.9414 | 2.8432 | 4.5432 | 26.3279 | 26.21 | Critical | 26.33 | Normal
320 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Deonari d3 | 100 | AL1531915 | 40 | 200/5 | 163.1966 | 154.9854 | 155.8311 | 121.6 | 192.8 | 152 | 1.547 | 155.4667 | 19.8447 | 29.8812 | 23.6863 | 73.4122 | 24.01 | Critical | 73.41 | Normal
321 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Jainpura dt27 | 100 | AL1531917 | 40 | 200/5 | 198.371 | 195.861 | 199.8738 | 122.8 | 152.4 | 0.4 | 3.4894 | 91.8667 | 24.36 | 29.8492 | 0.07995 | 54.2891 | 65.89 | Critical | 54.29 | Normal
322 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Jajau 1st sarsa raod DT01 | 100 | AL1531919 | 40 | 200/5 | 77.028 | 49.0193 | 102.585 | 143.6 | 263.6 | 133.6 | 3.1325 | 180.2667 | 11.0612 | 12.9215 | 13.7054 | 37.6881 | 46.23 | Critical | 37.69 | Normal
323 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Jio tower mandi mirja DT27 | 25 | AL1532053 | 10 | 50/5 | 185.1483 | 181.9682 | 184.3632 | 38.4 | 22.5 | 16.6 | 1.953 | 25.8333 | 7.1097 | 4.0943 | 3.0604 | 14.2644 | 48.65 | Critical | 57.06 | Normal
324 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245PFS | PAHAD FATEHPUR SIKARI_26154432245PFS | Agriculture | GULESTHA DUREX COMPLEX | 250 | AL1532055 | 80 | 400/5 | 221.8909 | 223.0175 | 226.2269 | 178.4 | 97.6 | 166.4 | 0.94398 | 147.4667 | 39.5853 | 21.7665 | 37.6442 | 98.996 | 20.98 | Critical | 39.6 | Normal
325 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Jio tower jautana | 25 | AL1532057 | 10 | 50/5 | 185.5243 | 188.2578 | 183.4034 | 21.5 | 0 | 21.3 | 2.1401 | 14.2667 | 3.9888 | 0 | 3.9065 | 7.8953 | 50.7 | Critical | 31.58 | Normal
326 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | Nagla mansa 3th dt07 chandrama ke ghar ke pass | 100 | AL1532202 | 40 | 200/5 | 189.1693 | 187.7038 | 0 | 24.4 | 36.4 | 90.8 | 1.5322 | 50.5333 | 4.6157 | 6.8324 | 0 | 11.4481 | 79.68 | Critical | 11.45 | Normal
327 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Jio tawer dt24 | 25 | AL1532205 | 10 | 50/5 | 184.2627 | 182.3379 | 186.735 | 17 | 40.1 | 26.7 | 2.0091 | 27.9333 | 3.1325 | 7.3118 | 4.9858 | 15.43 | 43.56 | Critical | 61.72 | Normal
328 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Neelam college dt17 | 63 | AL1532212 | 20 | 100/5 | 183.1047 | 178.4522 | 180.4173 | 0.2 | 97 | 33.4 | 4.2599 | 43.5333 | 0.036621 | 17.3099 | 6.0259 | 23.3724 | 122.82 | Critical | 37.1 | Normal
329 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Jajau jio tower DT02 | 25 | AL1532213 | 10 | 50/5 | 185.2006 | 181.7543 | 181.534 | 11.1 | 16.6 | 21.5 | 0.90117 | 16.4 | 2.0557 | 3.0171 | 3.903 | 8.9758 | 31.1 | Critical | 35.9 | Normal
330 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Mohhmadpur 3rd dauji pandit ji k ghar pr DT24 | 100 | AL1532214 | 40 | 200/5 | 184.7852 | 182.8104 | 191.9937 | 77.2 | 214 | 23.6 | 4.2514 | 104.9333 | 14.2654 | 39.1214 | 4.5311 | 57.9179 | 103.94 | Critical | 57.92 | Normal
331 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Arera 6th samsan ghat DT25 | 25 | AL1532216 | 20 | 100/5 | 165.0827 | 142.1562 | 165.9715 | 76 | 37.8 | 131.2 | 4.0666 | 81.6667 | 12.5463 | 5.3735 | 21.7755 | 39.6952 | 60.65 | Critical | 158.78 | Critical
332 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Didvaar 1 | 63 | AL1532217 | 20 | 100/5 | 162.8984 | 76.7282 | 161.7647 | 111.2 | 142 | 87.6 | 2.3625 | 113.6 | 18.1143 | 10.8954 | 14.1706 | 43.1803 | 25 | Critical | 68.54 | Normal
333 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Bharat petrolium chauma shahpur | 63 | AL1532218 | 20 | 100/5 | 186.8749 | 186.9845 | 185.6479 | 32.4 | 23 | 67.6 | 2.0361 | 41 | 6.0547 | 4.3006 | 12.5498 | 22.9052 | 64.88 | Critical | 36.36 | Normal
334 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Kheda jaat near by petrol pump DT33 | 250 | AL1532307 | 80 | 400/5 | 175.7923 | 179.3439 | 177.4169 | 356 | 181.6 | 312 | 1.9636 | 283.2 | 62.5821 | 32.5689 | 55.3541 | 150.505 | 25.71 | Critical | 60.2 | Normal
335 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Jajuo janangam 04 dt09 | 25 | AL1533781 | 10 | 50/5 | 183.7891 | 185.2965 | 183.0055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
336 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Jal nigam ke tubewell ke pass doora d2 | 25 | AL1533783 | 10 | 50/5 | 156.1855 | 155.8126 | 78.3615 | 0.1 | 23.8 | 22.5 | 2.3077 | 15.4667 | 0.015619 | 3.7083 | 1.7631 | 5.4871 | 53.88 | Critical | 21.95 | Normal
337 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | Bhagvan petrol pump 014 | 25 | AL1533786 | 10 | 50/5 | 192.1822 | 193.0982 | 195.3591 | 45.1 | 38.8 | 27.3 | 1.5633 | 37.0667 | 8.6674 | 7.4922 | 5.3333 | 21.4929 | 21.67 | Critical | 85.97 | Warning
338 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | Harshita resturent 017 | 25 | AL1533787 | 10 | 50/5 | 194.4037 | 195.792 | 196.2682 | 27.7 | 0 | 30.4 | 2.9144 | 19.3667 | 5.385 | 0 | 5.9666 | 11.3515 | 56.97 | Critical | 45.41 | Normal
339 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Near chakki new tf tehra Rawat | 100 | AL1533790 | 40 | 200/5 | 92.8172 | 231.1857 | 91.8484 | 84 | 181.2 | 78.4 | 2.5029 | 114.5333 | 7.7966 | 41.8908 | 7.2009 | 56.8884 | 58.21 | Critical | 56.89 | Normal
340 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | KELA DEVI KE KHET KE PASS | 63 | AL1533801 | 40 | 200/5 | 79.1794 | 180.7533 | 198.0076 | 116.4 | 40.4 | 125.2 | 2.019 | 94 | 9.2165 | 7.3024 | 24.7906 | 41.3095 | 33.19 | Critical | 65.57 | Normal
341 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Dyonari 1st DT 20 | 25 | AL1534095 | 10 | 50/5 | 162.2977 | 172.1668 | 170.5334 | 92.1 | 61.8 | 50.8 | 3.7046 | 68.2333 | 14.9476 | 10.6399 | 8.6631 | 34.2506 | 34.98 | Critical | 137 | Critical
342 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DDR | DAUDPUR_26154434632DDR | Agriculture | Daudpur 2nd pani ki tnki ke pss DT03 | 25 | AL1534101 | 10 | 50/5 | 185.3676 | 182.6764 | 181.0876 | 3.4 | 51.4 | 49.7 | 4.7173 | 34.8333 | 0.63025 | 9.3896 | 9.0001 | 19.0199 | 47.56 | Critical | 76.08 | Normal
343 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Dr. Ambedakar samudayik kendra siroli | 100 | AL1534104 | 40 | 200/5 | 42.3583 | 0 | 176.8603 | 97.2 | 168 | 116.8 | 1.5829 | 127.3333 | 4.1172 | 0 | 20.6573 | 24.7745 | 31.94 | Critical | 24.77 | Normal
344 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Nagla hunspura 1st DT 18 | 25 | AL1534109 | 10 | 50/5 | 172.3664 | 167.9097 | 165.9805 | 12.5 | 50.4 | 54.9 | 4.0339 | 39.2667 | 2.1546 | 8.4626 | 9.1123 | 19.7296 | 39.81 | Critical | 78.92 | Normal
345 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Deonari d2 | 25 | AL1534110 | 10 | 50/5 | 173.7361 | 163.4305 | 159.6844 | 32.3 | 38.7 | 61.2 | 2.6291 | 44.0667 | 5.6117 | 6.3248 | 9.7727 | 21.7091 | 38.88 | Critical | 86.84 | Warning
346 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | SHIVALAYA MANDIR KE PASS | 100 | AL1534183 | 40 | 200/5 | 202.194 | 212.6715 | 202.5314 | 138.4 | 0 | 61.2 | 3.0031 | 66.5333 | 27.9836 | 0 | 12.3949 | 40.3786 | 108.02 | Critical | 40.38 | Normal
347 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIA | KIRAWALI-3_26154424596KW3 | Agriculture | BUDDHA KE PLOT KE PASS | 100 | AL1534185 | 40 | 200/5 | 71.8688 | 200.082 | 199.355 | 164.4 | 54.8 | 114.4 | 2.3759 | 111.2 | 11.8152 | 10.9645 | 22.8062 | 45.5859 | 47.84 | Critical | 45.59 | Normal
348 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIA | KIRAWALI-3_26154424596KW3 | Agriculture | CAHAR HARDWARE KE PASS | 63 | AL1534188 | 20 | 100/5 | 201.9084 | 200.355 | 199.7945 | 107 | 77 | 79.4 | 1.4437 | 87.8 | 21.6042 | 15.4273 | 15.8637 | 52.8952 | 21.87 | Critical | 83.96 | Warning
349 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | VISHAL DHABA KE PASS | 63 | AL1534192 | 20 | 100/5 | 183.0676 | 187.4586 | 189.6055 | 47.2 | 0 | 45.4 | 2.3163 | 30.8667 | 8.6408 | 0 | 8.6081 | 17.2489 | 52.92 | Critical | 27.38 | Normal
350 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Jatav basti 2 | 100 | AL1534195 | 40 | 200/5 | 141.4239 | 138.1775 | 181.2723 | 92 | 158.8 | 129.6 | 1.4501 | 126.8 | 13.011 | 21.9426 | 23.4929 | 58.4465 | 25.24 | Critical | 58.45 | Normal
351 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIA | KIRAWALI-3_26154424596KW3 | Agriculture | ANGANVADI KENDRA KE PASS | 63 | AL1534197 | 20 | 100/5 | 189.6008 | 187.8274 | 187.3614 | 35 | 0.2 | 55 | 2.4016 | 30.0667 | 6.636 | 0.037565 | 10.3049 | 16.9785 | 82.93 | Critical | 26.95 | Normal
352 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245PFS | PAHAD FATEHPUR SIKARI_26154432245PFS | Agriculture | GAURAV KIRANA STORE KE SAMNE | 100 | AL1534200 | 40 | 200/5 | 224.1479 | 213.4559 | 218.3287 | 53.2 | 168 | 152.4 | 2.6962 | 124.5333 | 11.9247 | 35.8606 | 33.2733 | 81.0585 | 34.9 | Critical | 81.06 | Warning
353 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Toti ke khet ke pass nagla beech | 25 | AL1534362 | 10 | 50/5 | 167.4597 | 169.5047 | 168.9793 | 63.8 | 33.3 | 45.5 | 2.6589 | 47.5333 | 10.6839 | 5.6445 | 7.6886 | 24.017 | 34.22 | Critical | 96.07 | Critical
354 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | May. jio tower DT12 | 25 | AL1534363 | 10 | 50/5 | 169.7839 | 168.8106 | 171.8602 | 25.2 | 0.6 | 28.9 | 2.6643 | 18.2333 | 4.2786 | 0.10129 | 4.9668 | 9.3466 | 58.5 | Critical | 37.39 | Normal
355 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Vidarpur 1 | 25 | AL1534364 | 10 | 50/5 | 162.7896 | 157.4097 | 166.9542 | 62 | 74.2 | 9.8 | 5.925 | 48.6667 | 10.093 | 11.6798 | 1.6362 | 23.4089 | 52.47 | Critical | 93.64 | Critical
356 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | May 2nd pani ki tnki DT 13 | 100 | AL1534366 | 40 | 200/5 | 169.9451 | 167.0965 | 168.4794 | 113.6 | 61.2 | 96 | 1.1547 | 90.2667 | 19.3058 | 10.2263 | 16.174 | 45.7061 | 25.85 | Critical | 45.71 | Normal
357 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Mandi gud mandir ke pass 03 | 100 | AL1534367 | 40 | 200/5 | 172.2296 | 110.5437 | 71.4756 | 140.4 | 69.6 | 204 | 2.9112 | 138 | 24.181 | 7.6938 | 14.581 | 46.4559 | 47.83 | Critical | 46.46 | Normal
358 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Nagla beech d1 | 100 | AL1534370 | 40 | 200/5 | 168.9574 | 170.3585 | 168.5861 | 96 | 61.6 | 55.2 | 0.95016 | 70.9333 | 16.2199 | 10.4941 | 9.306 | 36.0199 | 35.34 | Critical | 36.02 | Normal
359 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245ISL | ISLAMGANJ_26154432245JJJ | Agriculture | RAM KISHAN COLONY ME | 100 | AL1534373 | 40 | 200/5 | 214.1512 | 217.4019 | 211.0324 | 78.8 | 55.6 | 91.6 | 0.79019 | 75.3333 | 16.8751 | 12.0875 | 19.3306 | 48.2932 | 21.59 | Critical | 48.29 | Normal
360 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Mahindra singh ji ke plot ke pass | 63 | AL1534378 | 20 | 100/5 | 185.9258 | 181.1884 | 183.0541 | 50.6 | 0 | 54.4 | 2.6302 | 35 | 9.4078 | 0 | 9.9581 | 19.366 | 55.43 | Critical | 30.74 | Normal
361 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Madanpura 1st DT17 | 25 | AL1534382 | 10 | 50/5 | 190.3283 | 188.0218 | 191.9539 | 13.7 | 21.6 | 0 | 1.893 | 11.7667 | 2.6075 | 4.0613 | 0 | 6.6688 | 83.57 | Critical | 26.68 | Normal
362 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Ngla kesriya 08 | 63 | AL1534383 | 20 | 100/5 | 171.876 | 170.1438 | 168.4995 | 23.2 | 40.8 | 107.8 | 3.8659 | 57.2667 | 3.9875 | 6.9419 | 18.1643 | 29.0936 | 88.24 | Critical | 46.18 | Normal
363 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DDR | DAUDPUR_26154434632DDR | Agriculture | Daudpur 8th jangi chauraha DT11 | 100 | AL1534386 | 40 | 200/5 | 184.084 | 187.41 | 183.9768 | 20 | 58 | 90.4 | 1.5258 | 56.1333 | 3.6817 | 10.8698 | 16.6315 | 31.183 | 61.05 | Critical | 31.18 | Normal
364 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632JAL | JAJOLI_26154434632JJL | Agriculture | School ke pass nagla Banjara dt04 | 63 | AL1534388 | 40 | 200/5 | 178.1322 | 192.5332 | 27.4972 | 181.6 | 0 | 103.2 | 3.944 | 94.9333 | 32.3488 | 0 | 2.8377 | 35.1865 | 91.29 | Critical | 55.85 | Normal
365 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Noorpur 1st 09 | 63 | AL1534452 | 10 | 50/5 | 171.4329 | 161.2106 | 170.8404 | 52.6 | 98.2 | 21.8 | 6.6577 | 57.5333 | 9.0174 | 15.8309 | 3.7243 | 28.5726 | 70.68 | Critical | 45.35 | Normal
366 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DDR | DAUDPUR_26154434632DDR | Agriculture | Daudpur pani ki tanki DT02 | 25 | AL1534453 | 10 | 50/5 | 183.2588 | 0.3741 | 184.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
367 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Madanpura 4th darav singh ke khet pr DT21 | 25 | AL1534454 | 10 | 50/5 | 190.8949 | 196.4768 | 190.4105 | 0 | 44.1 | 97.8 | 8.4833 | 47.3 | 0 | 8.6646 | 18.6221 | 27.2868 | 106.77 | Critical | 109.15 | Critical
368 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DDR | DAUDPUR_26154434632DDR | Agriculture | Daudpur 7th gopali ke ghr pr DT10 | 25 | AL1534455 | 10 | 50/5 | 170.1431 | 0 | 180.8549 | 97.9 | 42.6 | 43.5 | 5.4856 | 61.3333 | 16.657 | 0 | 7.8672 | 24.5242 | 59.62 | Critical | 98.1 | Critical
369 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Nagla ray singh airtel tower DT 13 | 25 | AL1534456 | 10 | 50/5 | 181.49 | 178.5481 | 179.237 | 12.4 | 20.2 | 16.4 | 0.67557 | 16.3333 | 2.2505 | 3.6067 | 2.9395 | 8.7966 | 23.67 | Critical | 35.19 | Normal
370 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DDR | DAUDPUR_26154434632DDR | Agriculture | Airtel tower daudpur | 25 | AL1534458 | 10 | 50/5 | 183.658 | 185.2839 | 184.9612 | 16.5 | 5.2 | 5.9 | 1.0967 | 9.2 | 3.0304 | 0.96348 | 1.0913 | 5.0851 | 79.35 | Critical | 20.34 | Normal
371 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Sikroda 3rd pokhar ke pas DT 42 | 25 | AL1534459 | 10 | 50/5 | 162.8475 | 160.2821 | 161.2778 | 24.6 | 83.4 | 42.2 | 5.2272 | 50.0667 | 4.006 | 13.3675 | 6.8059 | 24.1795 | 66.58 | Critical | 96.72 | Critical
372 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Devi ka adda | 25 | AL1534460 | 10 | 50/5 | 186.1221 | 0 | 186.3587 | 0.8 | 0 | 31.9 | 3.1508 | 10.9 | 0.1489 | 0 | 5.9448 | 6.0937 | 192.66 | Critical | 24.37 | Normal
373 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Ashok ke ghar ke pass | 25 | AL1534461 | 10 | 50/5 | 170.0707 | 168.2094 | 168.2386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
374 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | The grand regel restaurant choma shahpur | 25 | AL1534463 | 10 | 50/5 | 186.7788 | 0 | 183.9541 | 0 | 0 | 28.3 | 2.83 | 9.4333 | 0 | 0 | 5.2059 | 5.2059 | 200 | Critical | 20.82 | Normal
375 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Mukesh fauji ke makan ke pass | 63 | AL1534464 | 20 | 100/5 | 166.7384 | 167.3652 | 174.4494 | 120.8 | 68 | 0 | 5.2446 | 62.9333 | 20.142 | 11.3808 | 0 | 31.5228 | 91.95 | Critical | 50.04 | Normal
376 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | HC TEC HOTAL PAR | 63 | AL1534465 | 20 | 100/5 | 194.5884 | 193.1671 | 195.448 | 43.4 | 30.6 | 56.8 | 1.1346 | 43.6 | 8.4451 | 5.9109 | 11.1014 | 25.4575 | 30.28 | Critical | 40.41 | Normal
377 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | Jio tower Gopau dt10 | 25 | AL1534467 | 10 | 50/5 | 192.1717 | 192.8955 | 193.722 | 32.7 | 17.7 | 17.8 | 1.495 | 22.7333 | 6.284 | 3.4142 | 3.4483 | 13.1465 | 43.84 | Critical | 52.59 | Normal
378 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | UNDERA | 26154434913UDR | UNDERA_26154434913UDR | Agriculture | Appu ke khet ke pass | 25 | AL1534468 | 10 | 50/5 | 99.3597 | 164.9677 | 159.8362 | 2.4 | 62.4 | 0.5 | 6.0972 | 21.7667 | 0.23846 | 10.294 | 0.079918 | 10.6124 | 186.68 | Critical | 42.45 | Normal
379 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Jainpura 2nd DT 11 | 25 | AL1534469 | 10 | 50/5 | 204.3042 | 198.3694 | 199.2123 | 9.5 | 71.4 | 54.3 | 5.5367 | 45.0667 | 1.9409 | 14.1636 | 10.8172 | 26.9217 | 58.43 | Critical | 107.69 | Critical
380 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Jal nigam ke pass | 25 | AL1534470 | 10 | 50/5 | 189.1893 | 189.3819 | 188.2432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
381 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Arera 2nd DT20 | 100 | AL1534472 | 40 | 200/5 | 157.1841 | 156.7186 | 152.398 | 0.4 | 0.8 | 192.8 | 4.805 | 64.6667 | 0.062874 | 0.12537 | 29.3823 | 29.5706 | 198.14 | Critical | 29.57 | Normal
382 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Arera 3rd DT21 | 100 | AL1534474 | 40 | 200/5 | 158.777 | 162.7815 | 167.5883 | 206.8 | 0.8 | 0.8 | 5.15 | 69.4667 | 32.8351 | 0.13023 | 0.13407 | 33.0994 | 197.7 | Critical | 33.1 | Normal
383 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Ganga ram ji ke ghar ke samne | 25 | AL1534479 | 10 | 50/5 | 161.3849 | 159.7496 | 168.652 | 0 | 0 | 18.3 | 1.83 | 6.1 | 0 | 0 | 3.0863 | 3.0863 | 200 | Critical | 12.35 | Normal
384 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | TAJPUR NAGRIA | 22001434888TAJ | TAJPUR NAGARIYA_26154414888TPN | Agriculture | Dharmvir pani plant byara DT23 | 25 | AL1539336 | 10 | 50/5 | 163.4977 | 165.125 | 155.7725 | 15.4 | 1.8 | 38 | 3.1671 | 18.4 | 2.5179 | 0.29722 | 5.9194 | 8.7344 | 106.52 | Critical | 34.94 | Normal
385 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Samra 3rd airtel tower DT06 | 25 | AL1548291 | 10 | 50/5 | 188.4033 | 186.6911 | 185.6854 | 30.2 | 18.1 | 19.3 | 1.1547 | 22.5333 | 5.6898 | 3.3791 | 3.5837 | 12.6526 | 34.02 | Critical | 50.61 | Normal
386 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 26154434632SAM | SAMRA_26154434632SAR | Agriculture | Samra pani ki tanki ke pas DT15 | 25 | AL1548293 | 10 | 50/5 | 182.8473 | 183.7946 | 183.3691 | 32.2 | 0 | 0 | 3.22 | 10.7333 | 5.8877 | 0 | 0 | 5.8877 | 200 | Critical | 23.55 | Normal
387 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632JAL | JAJOLI_26154434632JJL | Agriculture | Shri bajrang bali garden & tent house ke pass | 63 | AL1548295 | 20 | 100/5 | 192.55 | 185.0599 | 191.0802 | 0 | 92 | 0 | 4.6 | 30.6667 | 0 | 17.0255 | 0 | 17.0255 | 200 | Critical | 27.02 | Normal
388 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DDR | DAUDPUR_26154434632DDR | Agriculture | Daudpur 1st dighbbar prdhan DT01 | 25 | AL1548296 | 20 | 100/5 | 183.1238 | 185.0188 | 186.1118 | 89.4 | 0 | 0 | 4.47 | 29.8 | 16.3713 | 0 | 0 | 16.3713 | 200 | Critical | 65.49 | Normal
389 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Matula ke khet ke pass | 25 | AL1548298 | 10 | 50/5 | 147.722 | 153.0352 | 152.9085 | 66 | 76.3 | 0 | 7.1707 | 47.4333 | 9.7497 | 11.6766 | 0 | 21.4262 | 60.86 | Critical | 85.7 | Warning
390 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632JAL | JAJOLI_26154434632JJL | Agriculture | Sabir buddhi ke ghar ke pass | 63 | AL1548300 | 20 | 100/5 | 191.4048 | 188.7774 | 193.3203 | 13.2 | 0 | 44 | 1.9554 | 19.0667 | 2.5265 | 0 | 8.5061 | 11.0326 | 130.77 | Critical | 17.51 | Normal
391 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | Jal nigam 2nd ikram nagar DT07 | 25 | AL1548362 | 10 | 50/5 | 177.3237 | 172.2201 | 179.179 | 15.1 | 52.4 | 15.1 | 3.73 | 27.5333 | 2.6776 | 9.0243 | 2.7056 | 14.4075 | 90.31 | Critical | 57.63 | Normal
392 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | Pokhar ke pass | 25 | AL1548363 | 10 | 50/5 | 175.343 | 175.9585 | 172.1173 | 14.9 | 0.1 | 57 | 5.1132 | 24 | 2.6126 | 0.017596 | 9.8107 | 12.4409 | 137.5 | Critical | 49.76 | Normal
393 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | VANSHIKA BEAUTY PARLOUR KE PASS | 25 | AL1548364 | 10 | 50/5 | 181.7673 | 0 | 182.237 | 21.3 | 8.7 | 29.1 | 1.7829 | 19.7 | 3.8716 | 0 | 5.3031 | 9.1747 | 47.72 | Critical | 36.7 | Normal
394 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | JAINGARA | 26154424533JAI | JAINGARA_26154424533JNG | Agriculture | Airtel tower school ke pass DT10 | 25 | AL1548365 | 10 | 50/5 | 176.6177 | 179.1981 | 173.6734 | 13.7 | 0 | 29.7 | 2.5747 | 14.4667 | 2.4197 | 0 | 5.1581 | 7.5778 | 105.3 | Critical | 30.31 | Normal
395 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MANGOLI KALA | 22001424654MGK | MANGOLI KALA_26154434654MGK | Agriculture | Manga dhiru 1 | 25 | AL1548366 | 10 | 50/5 | 178.8936 | 175.9731 | 179.0395 | 0 | 20.8 | 0 | 2.08 | 6.9333 | 0 | 3.6602 | 0 | 3.6602 | 200 | Critical | 14.64 | Normal
396 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Indus tower par | 25 | AL1548367 | 10 | 50/5 | 176.7235 | 182.3865 | 180.8514 | 48.6 | 0 | 0 | 4.86 | 16.2 | 8.5888 | 0 | 0 | 8.5888 | 200 | Critical | 34.36 | Normal
397 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Airtel tower basiya raymil DT12 | 25 | AL1548368 | 10 | 50/5 | 187.337 | 0 | 188.3865 | 18.5 | 0 | 12.6 | 1.6368 | 10.3667 | 3.4657 | 0 | 2.3737 | 5.8394 | 78.46 | Critical | 23.36 | Normal
398 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Nagla bich jio tower DT08 | 25 | AL1548369 | 10 | 50/5 | 186.6464 | 183.1196 | 187.473 | 12.1 | 12.4 | 0.6 | 1.1653 | 8.3667 | 2.2584 | 2.2707 | 0.11248 | 4.6416 | 48.21 | Critical | 18.57 | Normal
399 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855SHE | SHEETAL KUND_26154424855SLK | Agriculture | Jal nigam ki tanki hannu nagla DT20 | 25 | AL1548370 | 10 | 50/5 | 182.5919 | 186.1843 | 185.7742 | 32.9 | 30 | 18.8 | 1.2897 | 27.2333 | 6.0073 | 5.5855 | 3.4926 | 15.0854 | 20.81 | Critical | 60.34 | Normal
400 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632JAL | JAJOLI_26154434632JJL | Agriculture | Madanpura pahad ke pass | 63 | AL1548372 | 20 | 100/5 | 190.8765 | 181.237 | 186.3605 | 38.6 | 0 | 0 | 1.93 | 12.8667 | 7.3678 | 0 | 0 | 7.3678 | 200 | Critical | 11.69 | Normal
401 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Streets lights bharat pur agra road | 63 | AL1548373 | 20 | 100/5 | 131.9699 | 204.3231 | 132.0491 | 0.2 | 23.8 | 6.2 | 1.0623 | 10.0667 | 0.026394 | 4.8629 | 0.8187 | 5.708 | 136.42 | Critical | 9.06 | Normal
402 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855AKB | AKHBAI RURAL | Agriculture | MLA KE KHET KE PASS | 63 | AL1548375 | 20 | 100/5 | 182.1437 | 177.1847 | 179.9353 | 28.4 | 76.6 | 76.6 | 2.41 | 60.5333 | 5.1729 | 13.5723 | 13.783 | 32.5283 | 26.54 | Critical | 51.63 | Normal
403 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Nagla ray singh jio tower DT 11 | 25 | AL1548376 | 10 | 50/5 | 180.9386 | 178.408 | 180.8759 | 0.1 | 14.5 | 15.1 | 1.4709 | 9.9 | 0.018094 | 2.5869 | 2.7312 | 5.3362 | 52.53 | Critical | 21.34 | Normal
404 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | SHEETAL KUND | 26154424855AKB | AKHBAI RURAL | Agriculture | Nagla mahasukh harvir ke ghr ke pass DT09 | 100 | AL1548378 | 40 | 200/5 | 137.9404 | 182.6743 | 132.251 | 18.4 | 21.2 | 80 | 1.5062 | 39.8667 | 2.5381 | 3.8727 | 10.5801 | 16.9909 | 100.67 | Critical | 16.99 | Normal
405 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632JAL | JAJOLI_26154434632JJL | Agriculture | Sahanpur 2nd DT 05 | 63 | AL1548379 | 20 | 100/5 | 143.5293 | 188.9434 | 190.1754 | 143 | 90.6 | 40.8 | 4.4259 | 91.4667 | 20.5247 | 17.1183 | 7.7592 | 45.4021 | 56.34 | Critical | 72.07 | Normal
406 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | MADANPURA | 22001424632DAR | DABAR_26154434632DBR | Agriculture | Vijay pal master ji ke khet ke pass saray | 63 | AL1548380 | 20 | 100/5 | 182.2537 | 176.1022 | 180.3507 | 0.2 | 81 | 23.2 | 3.6053 | 34.8 | 0.036451 | 14.2643 | 4.1841 | 18.4849 | 132.76 | Critical | 29.34 | Normal
407 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245PFS | PAHAD FATEHPUR SIKARI_26154432245PFS | Agriculture | PRATHMIK VIDYALAYA KE BAHAR | 100 | AL5503942 | 40 | 200/5 | 218.5411 | 222.1856 | 220.0197 | 39.2 | 59.2 | 48.4 | 0.43347 | 48.9333 | 8.5668 | 13.1534 | 10.649 | 32.3692 | 20.98 | Critical | 32.37 | Normal
408 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Ved prakash ke ghar ke pass | 100 | AL5503944 | 40 | 200/5 | 206.0411 | 197.8964 | 204.1723 | 102.4 | 219.6 | 57.6 | 3.6223 | 126.5333 | 21.0986 | 43.4581 | 11.7603 | 76.317 | 73.55 | Critical | 76.32 | Normal
409 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Petrol pump dura 3 | 25 | AL5503945 | 10 | 50/5 | 141.2888 | 172.9218 | 148.1002 | 0.1 | 24.8 | 4.9 | 2.2684 | 9.9333 | 0.014129 | 4.2885 | 0.72569 | 5.0283 | 149.66 | Critical | 20.11 | Normal
410 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Shanti sthal 13 mori | 25 | AL5503947 | 10 | 50/5 | 202.4618 | 195.2537 | 198.7888 | 39.9 | 0 | 35 | 3.769 | 24.9667 | 8.0782 | 0 | 6.9576 | 15.0358 | 59.81 | Critical | 60.14 | Normal
411 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596GOA | GOPAU_26154424596GOP | Agriculture | AMBEDKAR PARK ME | 100 | AL5503950 | 40 | 200/5 | 188.4576 | 187.5172 | 0 | 82 | 91.2 | 0 | 2.1741 | 57.7333 | 15.4535 | 17.1016 | 0 | 32.5551 | 57.97 | Critical | 32.56 | Normal
412 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | INDRA SCHOOL KE PASS | 100 | AL5503994 | 40 | 200/5 | 228.4871 | 228.3396 | 229.8353 | 10 | 25.2 | 15.2 | 0.33451 | 16.8 | 2.2849 | 5.7542 | 3.4935 | 11.5325 | 50 | Critical | 11.53 | Normal
413 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596MAH | MAHUAR_26154424596MHR | Agriculture | Pura nagla mahuar dt09 | 63 | AL5503995 | 20 | 100/5 | 188.073 | 188.4952 | 189.1218 | 115.4 | 77.4 | 83.8 | 1.7619 | 92.2 | 21.7036 | 14.5895 | 15.8484 | 52.1416 | 25.16 | Critical | 82.76 | Warning
414 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245PFS | PAHAD FATEHPUR SIKARI_26154432245PFS | Agriculture | SBI BANK KE SAMNE | 63 | AL5503997 | 20 | 100/5 | 219.2033 | 222.8863 | 221.8564 | 37.2 | 28.6 | 18.4 | 0.81505 | 28.0667 | 8.1544 | 6.3745 | 4.0822 | 18.6111 | 32.54 | Critical | 29.54 | Normal
415 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245FAT | FATEHPUR SIKARI_26154432245FAT | Agriculture | Indra ghati 4th | 100 | AL5503998 | 40 | 200/5 | 153.4836 | 214.5843 | 0 | 50 | 112 | 89.6 | 1.3594 | 83.8667 | 7.6742 | 24.0334 | 0 | 31.7076 | 33.55 | Critical | 31.71 | Normal
416 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515441-EDSD I ACHNERA | 33/11 KV ACHHNERA | 26154412016ACH | ACHHNERA TOWN_26154412016ACH | Agriculture | SARKARI BUS STAND KE SAMNE | 100 | AL5503999 | 40 | 200/5 | 210.4711 | 220.6338 | 222.4071 | 136 | 216.4 | 101.6 | 2.5511 | 151.3333 | 28.6241 | 47.7452 | 22.5966 | 98.9658 | 43 | Critical | 98.97 | Critical
417 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Dedar school jajau dt14 | 25 | AL5504004 | 10 | 50/5 | 176.56 | 179.886 | 182.0614 | 45.3 | 0.1 | 40.8 | 4.3126 | 28.7333 | 7.9982 | 0.017989 | 7.4281 | 15.4443 | 57.66 | Critical | 61.78 | Normal
418 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Primary school ke pass sunhara 01 | 100 | AL5504006 | 40 | 200/5 | 183.3674 | 12.3654 | 182.398 | 81.6 | 132 | 86.8 | 1.2003 | 100.1333 | 14.9628 | 1.6322 | 15.8321 | 32.4272 | 31.82 | Critical | 32.43 | Normal
419 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Mahendra ke khet ke pass | 25 | AL5504079 | 10 | 50/5 | 22.8247 | 184.4555 | 190.1867 | 16.3 | 37.1 | 18.9 | 1.963 | 24.1 | 0.37204 | 6.8433 | 3.5945 | 10.8099 | 53.94 | Critical | 43.24 | Normal
420 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Karahitavar | 25 | AL5504511 | 10 | 50/5 | 183.6369 | 179.933 | 188.2826 | 20.7 | 44.6 | 0.6 | 3.8152 | 21.9667 | 3.8013 | 8.025 | 0.11297 | 11.9393 | 103.03 | Critical | 47.76 | Normal
421 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | NEW SURYA CITY COLONY 2 | 100 | AL5504514 | 40 | 200/5 | 194.9024 | 14.8635 | 196.959 | 0 | 1.2 | 0 | 0.03 | 0.4 | 0 | 0.017836 | 0 | 0.017836 | 200 | Critical | 0.02 | Normal
422 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Ambedkar park ke samne | 100 | AL5504515 | 40 | 200/5 | 132.4942 | 179.8399 | 169.834 | 0.8 | 86.4 | 88 | 2.1603 | 58.4 | 0.106 | 15.5382 | 14.9454 | 30.5896 | 50.68 | Critical | 30.59 | Normal
423 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472NGR | NAGAR_26154434472NGR | Agriculture | Supera 1st DT 12 | 25 | AL5504516 | 10 | 50/5 | 203.6366 | 199.308 | 199.2006 | 31.9 | 66.8 | 55.8 | 3.0905 | 51.5 | 6.496 | 13.3138 | 11.1154 | 30.9252 | 29.71 | Critical | 123.7 | Critical
424 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Jajuo janangam second dt07 | 25 | AL5504517 | 10 | 50/5 | 183.7615 | 185.7172 | 184.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
425 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | FATEHPUR SIKRI IPDS | 26154434472CMA | CHOMA_26154434472CMA | Agriculture | Daru Kara Sarkari school | 100 | AL5504519 | 10 | 50/5 | 188.8959 | 190.4521 | 182.2899 | 0 | 0 | 65.4 | 6.54 | 21.8 | 0 | 0 | 11.9218 | 11.9218 | 200 | Critical | 11.92 | Normal
426 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | GOVT TUBEL PAR | 25 | AL5504521 | 10 | 50/5 | 195.1952 | 193.781 | 195.8285 | 0 | 0 | 10 | 1 | 3.3333 | 0 | 0 | 1.9583 | 1.9583 | 200 | Critical | 7.83 | Normal
427 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463SAR | SARSA_26154434463SAS | Agriculture | Dithwar dt1 | 25 | AL5504522 | 10 | 50/5 | 172.4728 | 173.145 | 172.8843 | 21 | 46.2 | 21.7 | 2.4857 | 29.6333 | 3.6219 | 7.9993 | 3.7516 | 15.3728 | 55.91 | Critical | 61.49 | Normal
428 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | DOORA | 22001424463JAJ | JAJAU_26154434463JJU | Agriculture | Jajuo janangam 05 dt13 | 25 | AL5504524 | 10 | 50/5 | 184.0366 | 189.9876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Critical | 0 | Normal
429 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIA | KIRAWALI-3_26154424596KW3 | Agriculture | NAYARA PETROL PUMP PAR | 25 | AL5504526 | 10 | 50/5 | 200.8583 | 196.4735 | 199.6082 | 0 | 30.4 | 0 | 3.04 | 10.1333 | 0 | 5.9728 | 0 | 5.9728 | 200 | Critical | 23.89 | Normal
430 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Ro plant ke pass | 63 | AL5504528 | 20 | 100/5 | 168.2626 | 127.4232 | 131.9032 | 116 | 0 | 0 | 5.8 | 38.6667 | 19.5185 | 0 | 0 | 19.5185 | 200 | Critical | 30.98 | Normal
431 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | Maharaj Singh ke khet ke pass | 25 | AL5504530 | 10 | 50/5 | 193.3756 | 192.072 | 194.031 | 0 | 0 | 42.6 | 4.26 | 14.2 | 0 | 0 | 8.2657 | 8.2657 | 200 | Critical | 33.06 | Normal
432 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 26154432245OLE | OLENDA_26154432245OLE | Agriculture | Maharaj Singh ke khet ke pass 2 | 63 | AL5504585 | 20 | 100/5 | 195.7369 | 197.1022 | 193.054 | 28.2 | 27.4 | 56 | 1.4104 | 37.2 | 5.5198 | 5.4006 | 10.811 | 21.7314 | 50.54 | Critical | 34.49 | Normal
433 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515443-EDSD III FATEHPUR SIKRI | 33/11 KV FATEHPUR SIKARI | 22001422245MAN | MANDI MIRZA_26154432245MAN | Agriculture | Nagala device 1st dt01 | 25 | AL5504589 | 10 | 50/5 | 177.531 | 82.2272 | 102.7057 | 70.6 | 0 | 0 | 7.06 | 23.5333 | 12.5337 | 0 | 0 | 12.5337 | 200 | Critical | 50.13 | Normal
434 | DVVNL | Agra | AGRA II | EDC AGRA | EDD KIRAWALI AGRA | 2515442-EDSD II KIRAWALI | KIRAWALI | 26154414596KIA | KIRAWALI-3_26154424596KW3 | Agriculture | BIHARI JI BILDING METERIAL KE SAMNE | 63 | AL5504590 | 20 | 100/5 | 201.0175 | 198.813 | 194.6824 | 36 | 30 | 74 | 2.0664 | 46.6667 | 7.2366 | 5.9644 | 14.4065 | 27.6075 | 58.57 | Critical | 43.82 | Normal
Applied filters: Discom is DVVNL Circle_Name is EDC AGRA Division_Name is EDD KIRAWALI AGRA Latest Date is Latest Date Unbalancing_Status is Critical Discom is DVVNL Circle_Name is EDC AGRA Division_Name is EDD KIRAWALI AGRA Latest Date is Latest Date DateOffset is less than 0